CEMDPS User Guide

Table of Contents

5What is CEMDPS?


5Overview


8System Components


9Help


9Online Help System


10Off-line Help Documents


11Navigating the Site


11Navigation Overview


12Left Menu Bar


13Breadcrumbs


14Common Footer Links


15Date Selection


17Starting and Managing Processes


17Facility Home Page


23Delete <Item> Page


24Download Synchronization Files


25Work Item Assignment Report


27Upload EDR Submittal Packet


27Monitoring Plan Upload


30Test Protocol Upload


33Certification Reports Upload


36Quarterly Reports Upload


41Facility Configuration


41Facility Configuration


44View Source Combination


47View Emission Result


55View CEMS


59View Analyzer


63Monitoring Plans


63Monitoring Plan Page


71Monitoring Plan Submittal Page


74Add Note Page


75View Notes Page


76Record Keeping Information


76Edit Record Keeping Information (EDR 841)


80QA Information


80Edit Monitoring Plan QA Information (EDR 842)


86Configuration Information


86Source Combinations


95Emission Results


113CEMS


119Analyzers


133Test Protocols


133Test Protocol


139Create/Edit Submitter Information (EDR 801/802)


141Set Proposed Testing Date (EDR 803)


142Create/Edit Test Firm (EDR 803/804)


144Create/Edit Analytical Laboratory (EDR 805/806)


146Edit CEMS to Be Tested List (EDR 807)


148Test Protocol Submittal Page


151Certification Reports


151Certification/Test Report Page


157Certification Report/Test Results Submittal Page


160Set Test Date Page


161CEMS


161Add Tested CEMS (EDR 844)


164Edit Tested CEMS (EDR 844)


165Non-Opacity RATA Test Data List (EDR 852)


167Set Non-Opacity RATA Test Data (EDR 852)


169Opacity RATA Test Data List (EDR 856)


170Set Opacity RATA Test Data (EDR 856)


172DAS Test Data List (EDR 878)


174Set DAS Test Data (EDR 878)


176Set Operational Test Period Information (EDR 876)


177Analyzers


177Add Tested Analyzer (EDR 848)


179Edit Tested Analyzer (EDR 848)


1807-Day Calibration Error Data List (EDR 868)


181Edit 7-Day Calibration Error Data (EDR 868)


183Cycle Time Data List (872)


184Edit Cycle Time Data (EDR 872)


186Linearity Data List (EDR 860)


186Edit Linearity Data (EDR 860)


189Correspondence


189CEMDPS Correspondence


191Find User Pop-Up


193Select Users Pop-Up


194Messages Page


195Index





What is CEMDPS?

Overview

Welcome to the Continuous Emission Monitoring Data Processing System (the CEMDPS).  The CEMDPS allows you to record and edit the continuous emissions monitoring system information you are required to provide to the DEP.  Through a simple system of Web pages, you can submit and manage monitoring plans, test protocols, certification reports, and emission reports. You can also upload your quarterly report EDR documents to the CEMDPS for review by the DEP.  The CEMDPS automatically routes your information to the appropriate DEP personnel for review and approval. 

The user guide begins by introducing you to the CEMDPS and how to navigate it, then describes each screen used to create and edit monitoring plans, test protocols, certification reports, and quarterly reports.

Important note

Opacity monitor performance specification tests are inconsistently referenced in several places throughout Revision 8 of the Continuous Source Monitoring Manual (CSMM), the new CEMDPS, and in the instructions provided throughout this manual.  Performance testing for opacity must be conducted in accordance with the tests and procedures in Attachment No. 1 of the CSMM, not using the tests specified in 40 CFR, Part 75, Appendix A.  This inconsistency was discovered after the CSMM was finalized and the CEMDPS in the final stages of development.  To properly correct the errors, a new revision of the CSMM would need to be drafted and approved and the CEMDPS reprogrammed to accommodate the changes.

Because such a process would delay the implementation of the CEMDPS for an indeterminable period of time, work a rounds have been established to capture and evaluate submitted data until such changes are completed.  The impacted record types will in most cases be able to accept the data required to evaluate compliance.  For those instances in which this is not the case, electronic attachments may be required to be submitted to the Department.  Please contact the Chief of the CEM Section if you require assistance.
The following is a summary of the record types that have been identified as being impacted by the inconsistencies and the recommended course of action:
RT 829:  Monitoring Plan Analyzer Information II

Inconsistency:  Start Col 165 and 171 require the submittal of a linearity limit for both opacity and non-opacity analyzers.  Opacity analyzers are required to conduct a calibration error test, not a linearity test.

Correction:  A calibration error limit should be reported for opacity analyzers in accordance with the format specified in the instructions.  Non-opacity analyzers should be handled as stated in the record type.

RT 830:  Monitoring Plan Calibration Error Limit Information 

Inconsistency:  Start Col 83, 89, and 95 require the submittal of a calibration error limit for both opacity and non-opacity analyzers.  Opacity analyzers are required to conduct a zero and calibration drift-24 hour test, not a calibration error test.

Correction:  A zero and calibration drift-24 limit should be reported for opacity analyzers in accordance with the format specified in the instructions.  Non-opacity analyzers should be handled as stated in the record type.

RT 840:  Monitoring Plan Opacity and Non-Opacity Analyzer Specification Information II
Inconsistency:  Start Col 81 and 87 require the submittal of manufacturer’s claimed linearity for both opacity and non-opacity analyzers.  Opacity analyzers are required to conduct a calibration error test, not a linearity test.

Correction:  The manufacturer’s claimed calibration error should be reported for opacity analyzers in accordance with the format specified in the instructions.  Non-opacity analyzers should be handled as stated in the record type.

Inconsistency:  Start Col 100, 106, and 112 require the submittal of manufacturer’s claimed 7-day calibration error for both opacity and non-opacity analyzers.  Opacity analyzers are required to conduct a calibration drift-24 hour test, not a 7-day calibration error test.

Correction:  The manufacturer’s claimed zero and calibration drift-24 hour should be reported for opacity analyzers in accordance with the format specified in the instructions.  Non-opacity analyzers should be handled as stated in the record type.

Inconsistency:  Start Col 125 requires the submittal of manufacturer’s claimed cycle time for both opacity and non-opacity analyzers.  Opacity analyzers are required to conduct a system response time test, not a cycle time test.

Correction:  The manufacturer’s claimed system response time should be reported for opacity analyzers in accordance with the format specified in the instructions.  Non-opacity analyzers should be handled as stated in the record type.

RT 842:  Monitoring Plan QA Information

Inconsistency:  Calibration error and linearity check information is required for both opacity and non-opacity analyzers.  Opacity analyzers are required to conduct zero and calibration drift-24 hour and calibration error checks, not calibration error and linearity checks.
Correction:  Replace calibration error check with zero and calibration drift-24 hour check for opacity analyzers.  Replace linearity check with calibration error check for opacity analyzers.  Non-opacity analyzers should be handled as stated in the record type.

RT 844:  Certification Report CEMS Test Completion Date

Inconsistency:  Start Col 71 requires the type of testing to be identified for opacity and non-opacity CEMSs.  Tests for opacity and non-opacity CEMSs should be identified differently.

Correction:  The words “Relative accuracy test audit for initial cert.” should read “Relative accuracy test for initial cert.” and “Annual relative accuracy test audit” should read “Annual relative accuracy test” for opacity CEMSs.  Non-opacity CEMSs should be handled as stated in the record type.    

RT 848: Certification Report Analyzer Test Completion Date

Inconsistency:  Start Col 73 requires the type of testing to be identified for opacity and non-opacity analyzers.  Tests for opacity and non-opacity analyzers should be identified differently.

Correction:  The words “Linearity testing” should read “Calibration error testing”.  The words “Cycle time testing” should read “Response time test” and “7-day calibration error testing” should read “zero and calibration drift-24 hour check” for opacity analyzers.  Non-opacity analyzers should be handled as stated in the record type.

RT 860:  Certification Report Linearity Data

Inconsistency:  The record type requires linearity test data for opacity and non-opacity analyzers.  Tests for opacity and non-opacity analyzers should be identified differently.

Correction:  Calibration error test results should be entered for opacity analyzers instead of linearity test results.  Non-opacity analyzers should be handled as stated in the record type.

RT 868:  Certification Report 7-Day Calibration Error Data

Please note that this information should only be submitted for non-opacity analyzer 7-day calibration error test runs.  Opacity zero and calibration drift-24 hour test results will need to be submitted as an attachment to the test report submittal.  Please contact the Chief of the CEM Section for instructions.

RT 872:  Certification Report Cycle Time Data

Please note that cycle time test data should be submitted for non-opacity analyzers and response time test data should be submitted for opacity analyzers.  Start Col 83 will accommodate 1-5 periods for use in reporting test information.

RT 888:  Emission Data Report Linearity Results
Please note that linearity results should be submitted for non-opacity analyzers and calibration error test results should be submitted for opacity analyzers.
System Components

The CEMDPS provides facility users with a set of customized pages to submit and maintain continuous emissions monitoring system information to the DEP.  A separate component is available for DEP staff to review, manage, analyze, and report the continuous emissions data.

The system provides separate pages for creating, editing and submitting monitoring plans, test protocols, and certification reports.  The CEMDPS also allows you to enter basic information for quarterly reports and upload the quarterly report EDRs.  

Note:  The CEMDPS does not provide a web interface for creating and managing quarterly reports online.  It provides the capability to enter basic quarterly report data and to upload your quarterly report EDR documents to the web for review by the DEP.  

The CEMDPS is comprised of the following main components:

· Data entry pages for use by facility users
· Automated data validation and data checking

· Integrated online user Help
· Electronic document attachment capability

· Note system to communicate information to and from the DEP staff

· Online submission process
· Review pages for use by the DEP staff

· Accept/Reject pages for use by the DEP staff

· Revision pages for use by facility users
Help

Online Help System

The CEMDPS includes an integrated, online Help system complete with Search capability.  This Help system provides page and field-level information to assist you in submitting and updating your facility's monitoring plans, test protocols, and certification reports.  Each page in the CEMDPS provides a direct link to online Help for that page and a method to contact appropriate DEP staff for additional assistance.  Click the Help link at the bottom of the page to access online Help.  This link opens the online Help window and displays Help information specific to the current page.  You can also browse the Help contents or search for answers to general or specific questions about the system.

Off-line Help Documents

In addition to online Help, the CEMDPS also provides off-line user help that can be downloaded to your PC or printed.  The offline Help file can be downloaded from a link in the online Help.
· Click Download Off-line Help Documentation to your PC to access the entire CEMDPS Help file.  You can download the file in HTML format and save the file on your PC.  You can then access the  Help file at anytime, even if you are not logged into the system.

· Click Download Printable MS Word User Manual to view, save, and/or print the CEMDPS Help file in Microsoft Word © format.

· Click Download Printable PDF User Manual to view, save, and/or print the CEMDPS Help file in PDF format.

Navigating the Site

Navigation Overview

The CEMDPS provides a system of menus, buttons, and links to move through the continuous emissions reporting process.  

At the top of most pages in the CEMDPS, BACK (  ←  ) and FORWARD (   →  ) buttons appear in the taskbar.  Although these buttons are common navigational devices in most web sites, they are not the recommended method of page navigation for the CEMDPS.  If you use the Back or Forward button on your toolbar to move between pages in the CEMDPS, you run the risk of losing data that was not saved (data that was previously saved will not be affected) and encountering "Page not available" errors.  In addition, if you use the Back button, the links on the page you go back to may not function properly.  If this occurs, click Refresh [image: image1.jpg]


 to refresh the page and enable the links.

Note: Do not use the  BACK (  ←  ) and FORWARD (   →  ) buttons to move between CEMDPS pages.  Instead, use the built-in navigational buttons and links that are provided. 

Unfortunately, it is not possible to deactivate the Back/Forward buttons in the application, but it is possible to remove them from your page display. These buttons are part of the Standard Buttons toolbar.  To remove the Back/Forward buttons from your page display, click View on the main toolbar and select Toolbars.   A drop down menu of toolbars will appear on the right.  A checkmark will appear to the left of any toolbar that is currently displayed.  If the Back/Forward buttons are currently displayed on your page, a checkmark will appear to the left of Standard Buttons.  Click Standard Buttons.  The page will immediately display without the Standard Buttons toolbar.

This toolbar also includes a number of buttons, such as Refresh and Print, that you may want to use.  If you need access to a button on the Standard Buttons toolbar, simply select View>Toolbars>Standard Buttons.  A checkmark will appear to the left of Standard Buttons and the page will display with the Standard Buttons toolbar.

For more information on the CEMDPS's system of menus, buttons, and links, see Left Menu Bar, Breadcrumbs, and Common Footer Links.

Left Menu Bar

Each page in the CEMDPS includes a menu bar with links to common activities and important information within the online system.  The menu displays on the left side of each page.  The following sections describe the links available on the left menu bar.

[image: image2.jpg]Quick Links.

~Hame,
- Create Synchvonization Files

- Send Message

- View allMessages

2008-11-27 00:00:000
From: INTUSER

To: EXTUSER
2008-11-27 00:00:000
From: INTUSER

To: EXTUSER

his s 3 longersubject





Quick Links

Quick Links offer a fast way to access common pages in the CEMDPS.

	Link
	Description

	Home
	Returns you to the CEMDPS facility home page.

	Create Synchronization Files
	Opens the Download Synchronization Files page, which allows users using the CEMDPS disconnected client application to download the latest internal DEP codes file and configuration file.


Correspondence and Inbox

The Correspondence and Inbox areas, which appear under the Left Menu Bar, provide access to the CEMDPS messaging system.  See Correspondence and Inbox for more information.

Breadcrumbs

As you navigate through the CEMDPS pages, a set of links displays at the top of each page. These links, typically called breadcrumbs, indicate the path you took to reach the current page and provide links for returning to previous pages. For example, if you are on the Edit Source Combination page, the header path links might be as follows:

Home --> Edit Monitoring Plan --> Edit Source Combination 

This path indicates that you began on the Home page, then went to the Edit Monitoring Plan page, and are currently on the Edit Source Combination page.  As the current page, the final page in the path is not a link.  All previous pages are links back to those pages.  These links, along with the CEMDPS's buttons and left menu bar, are the recommended method for moving within pages of the CEMDPS application.  

Note: Do not use the  BACK (  ←  ) and FORWARD (   →  ) buttons in your browser to move between the CEMDPS pages.  Instead, use the built-in navigational buttons and links that are provided. 

Common Footer Links

In the footer section of the CEMDPS pages, links are provided to access the DEP Home Page, BAQ Home Page, DEP contact information, and online Help and also to logout of the system and e-mail the DEP Help Desk. 

[image: image3.jpg]PA Dept.of Enviranmantal Protection DEP Home | CEM Home | Contacts | Helpl Logout |

For assistance, please call DEP at (717) 705-3768
between the hours of £:00 AM to 430 PM or send an e-mailto
ep-efactshelpdeskteam@state.pa.us.





	Link
	Description

	DEP Home


	Links to the DEP Home Page (www.dep.state.pa.us)

	CEM Home
	Links to the DEP Bureau of Air Quality's Continuous Emission Monitoring Home Page (http://www.dep.state.pa.us/dep/deputate/airwaste/aq/cemspage/cems.htm)

	Contacts
	Links to the DEP Bureau of Air Quality's Continuous Emission Monitoring contact page (http://www.dep.state.pa.us/dep/deputate/airwaste/aq/cemspage/contact.htm)

	Help
	Displays a help window describing the options available on the page.

	Logout
	Logs you out of the CEMDPS

	ep-efactshelpdeskteam@state.pa.us
	Opens a message in your default e-mail program that is automatically addressed to the eFacts Help Desk.


Date Selection

You can access the date selection calendar from any date field in the CEMDPS that displays the calendar icon [image: image4.jpg]


.  Clicking the calendar icon displays a calendar next to the date field and lets you click a date in the calendar to enter that date in the date field.  The following table describes each part of the date selection calendar.

[image: image5.jpg]0570672007 2| st be mavddyyyy)

[ [ vz v] B3
Wak Mon Tue Wed Thu F Sat Sun
18 1z 34 s o
w7 s @ 2o
2 14 18 8 e w2
2 2 2 o2 o om o
2 = m ow on

Man. 22. Jan 2007





	Date Picker Element
	Description

	Right/Left Arrows [image: image6.jpg]



	Click the right arrow to display the next month and the left arrow to display the previous month.

	Month Drop-Down List [image: image7.jpg]



	Click the month drop-down list to pick the month.

	Year Drop-Down List [image: image8.jpg]



	Click the year drop-down list to pick the year.

	Dates
	Once you navigate to the correct month and year, click any date to enter it into the date field.  If there is already a date entered in the date field, that date displays in red in the calendar.

	Today's Date
	Today's date always displays at the bottom of the calendar.  Click today's date to enter it in the date field.


Starting and Managing Processes

 XE "View/Send Correspondence " \* MERGEFORMAT 

 XE "View/Edit Details " \* MERGEFORMAT 

 XE "View History " \* MERGEFORMAT 

 XE "Upload EDR Submittal Packet " \* MERGEFORMAT 

 XE "Upload Client Application Submittal Packet " \* MERGEFORMAT 

 XE "Type " \* MERGEFORMAT 

 XE "Test Protocols " \* MERGEFORMAT 

 XE "Status " \* MERGEFORMAT 

 XE "Replace with EDR Upload " \* MERGEFORMAT 

 XE "Remove <Item> " \* MERGEFORMAT 

 XE "Online Facility " \* MERGEFORMAT 

 XE "Offline Client Application " \* MERGEFORMAT 

 XE "Monitoring Plans " \* MERGEFORMAT 

 XE "Facility Action Required " \* MERGEFORMAT 

 XE "Emission Result " \* MERGEFORMAT 

 XE "Emission Reports " \* MERGEFORMAT 

 XE "Download Facility Configuration Data " \* MERGEFORMAT 

 XE "DEP Action Required " \* MERGEFORMAT 

 XE "Certification/Test Reports " \* MERGEFORMAT 

 XE "CEMSID " \* MERGEFORMAT Facility Home Page

Once you log into the CEMDPS, the Facility page displays and serves as the home page for the system.  This page provides information about processes in progress at your  facility and lets you start new processes, such as monitoring plans and test protocols. The name of your company, the facility, and the facility ID display at the top of the page.

[image: image9.jpg]~ Commonwealth of Pennsylvania "
ent of Environmental Protection

Bureau of Air Quality.

- Send Message
- View AllMessages

T mbox

| 2006-11-27 om.0m008
 From: NTUSER
To: EXTUSER

From: INTUSER.
To: EXTUSER

Expand Al | Collapse All

& Start New Process
Glick the B button to expand

& Active Processes
Glick the B button to expand

CASTLE RUBBERLLC
CASTLE RUBBER LLC/EAST BUTLER BORO
Primary Facilty ID: 510331

& Configuration Information

Glick the Bl button to expand

PADapt of Environmental Prtection

DEP Home | CEM Home | Contacts | Help | Logout]

For assistance, please call DEP at (717) 7053768
between the hours of £:00 AM to 4:30 PM or send an e-mail to
ep-efactshelpdeskteam@state. pa.u





Navigating the Facility Home Page

The Facility home page contains three sections, Start New Process, Active Processes, and Configuration Information, which are expandable and collapsible.  Using the expand (+) and collapse (-) symbols, you can display or hide information in these three sections.

· Click the plus sign (+) in front of any heading to view more detailed information about that heading or to access more options.  Information and available options display indented beneath the expanded heading.

· Click the minus sign (-) in front of any heading to collapse (hide) the details displayed beneath it.

· Click the Expand All link to display all information and options beneath all headings at once.

· Click the Collapse All link to collapse the entire hierarchy of information, hiding all details except for the three main headings.

Descriptions of the information and options available under each of the main sections (Start New Process, Active Processes, and Configuration Information) follow in the sections below.

Start New Process

When you want to create a brand new monitoring plan, test protocol, certification/test report, or emission report, use the options under the Start New Process heading.  The Start New Process links allow you to use a series of screens in the application to create a new monitoring plan, test protocol, test report, or emission report or to upload a text file containing the information for the new item.

Note:  If you want to continue working on a monitoring plan, test protocol, test report, or emission report that you previously started (but have not yet submitted), find that item in the Facility Action Required section under the Active Processes heading and click the View/Edit Details link.  See Active Processes below for more information.

When you expand (+) the Start New Process heading, a list of links displays. These links offer two methods of entering information into the CEMDPS:  typing information into an online interface or uploading EDR files.  The table below describes these options.

[image: image10.jpg]& Start New Process
Onine Facity

Wontoring Plan
Test Protocal
CertficationfTest Report
Enission Report

Upload EDR Submital Packet

Wontoring Plan
Test Protocal
CertficationfTest Report
Emission Report




	Heading/Link
	Description

	Online Facility
	The links under this heading are for facilities who perform all continuous emission reporting processes (monitoring plans, test protocols, certification/test reports) using the CEMDPS online interface.  

	Monitoring Plan
	This link goes to the Monitoring Plan page and lets you enter monitoring plan data and submit the monitoring plan through a set of web pages.

	Test Protocol
	This link goes to the Test Protocol page and lets you enter test protocol data and submit the protocol through a set of web pages.

	Certification/Test Report
	This link goes to the Certification/Test Report page and lets you enter certification and test data and submit them through a set of web pages.

	Emission Report
	This link goes to the Quarterly Reports Upload page and lets you upload a file containing your quarterly report or sample quarterly report to the CEMDPS.

Note:  The CEMDPS system provides screens for entering data for all continuous emission reporting except for quarterly reports.  Quarterly reports must be uploaded as a file.

	Upload EDR Submittal Packet
	If your facility does not perform all continuous emission reporting processes using the CEMDPS online data entry screens, the links under this heading allow you to upload documents containing your EDRs  

	Monitoring Plan
	Use this link if your facility does not perform all continuous emission reporting processes using the CEMDPS online data entry screens.  This link opens the Monitoring Plan Upload page and lets you upload a file containing your monitoring plan EDRs.

	Test Protocol
	Use this link if your facility does not perform all continuous emission reporting processes using the CEMDPS online data entry screens. This link opens the Test Protocol Upload page and lets you upload a file containing your test protocol EDRs. 

	Certification/Test Report
	Use this link if your facility does not perform all continuous emission reporting processes using the CEMDPS online data entry screens. This link opens the Certification Reports Upload page and lets you upload a file containing your certification/test report EDRs. 

	Emission Report
	This link goes to the Quarterly Reports Upload page and lets you upload a file containing your quarterly report or sample quarterly report to the CEMDPS.


Active Processes

The Active Processes section contains lists of monitoring plans, test protocols, test reports, and emission reports in various stages of the creation and submission process.  The Facility Action Required area displays all items that have not yet been submitted for review by the DEP or which require DEP requested revisions.  If you previously created a new monitoring plan, test protocol, test report, or emission report using the options under the Start New Process heading, but have not yet submitted it to the DEP, that item appears in the Active Processes section under Facility Action Required.  You can click the View/Edit Details link for that item to continue entering information and to submit the item for DEP's review.  All submitted monitoring plans, test protocols, test reports, and emission reports awaiting DEP action appear under the DEP Action Required heading in the Active Processes section.

When you expand (+) the Active Processes heading, you can view information about actions required by your facility and actions required by the DEP regarding monitoring plans, test protocols, certification reports, and emission reports.  Descriptions of options listed under active processes appear in the table below.

[image: image11.jpg]= Active Processes

& [Facility Action Required

& Monit

g Plans (1)

[Monitori

g Plan £120 Revision

 ViewiEdt Detals
o SendMessage

o View Al Messages

o View History

© Remove Monioring Plan
‘@ Replace With EDR Uploa

[Monitori

g Plan £182 Revision

ViewEdt Detals
Send lessage

View All\essages
View Hitary

Remave hontoring Plan

‘@ Replace With EDR Uploa

[Monitoring Plan #199 - First Test Monitoting Plan created by us Initiated

ViewEdt Detals
Send lessage

View All\essages
View Hitary

Remave hontoring Plan

‘@ Replace With EDR Uploa

[Monitori

g Plan £270 - Workshop Mon

ng Plan In

 ViewiEdt Detals
o SendMessage

o View Al Messages

o View History

© Remove Monioring Plan
 Replace With EDR Uploa!

B Test Protocols (30)
Glick the 3 button to expand

B Centification/Test Reports (17)
Glick the 5 button to expand

& Emission Reports (38)
Glick the 5 button to expand

& [DEP Action Required

E Monitoring Plans (1)

[Monitoring Plan £39 Review

View Detals
Send lessage
View All\essages
Vigw Hitary

B Test Protocols (11)
Glick the 3 button to expand

B Centification/Test Reports (12)
Glick the 5 button to expand

& Emission Reports (10)
Glick the 5 button to expand





	Option
	Description

	Facility Action Required
	Expanding (+)  this option lets you view and edit information in monitoring plans, test protocols, certification reports, and emission reports that have not yet been submitted for review by the DEP or which require DEP requested revisions.

	DEP Action Required
	Expanding (+)  this option lets you view information about your facility's monitoring plans, test protocols, certification reports, and emission reports that are awaiting the DEP's review and action.  When you view items under DEP Action Required, the information displays in read-only screens.  You may not edit any information for items under DEP Action Required.

	Monitoring Plans
	Expanding (+) this option displays a list of your facility's monitoring plans and links allowing you to view or take action (for Facility Action Required items only) on them.  The number of monitoring plans for your facility appears in parentheses next to this option. 

	Test Protocols
	Expanding (+) this option displays a list of your facility's test protocols and links allowing you to view or take action (for Facility Action Required items only) on them.  The number of test protocols for your facility appears in parentheses next to this option. 

	Certification Reports
	Expanding (+) this option displays a list of your facility's certification reports and links allowing you to view or take action (for Facility Action Required items only) on them.  The number of certification reports for your facility appears in parentheses next to this option. 

	Emission Reports
	Expanding (+) this option displays a list of your facility's emission reports and links allowing you to view or take action (for Facility Action Required items only) on them.  The number of emission reports for your facility appears in parentheses next to this option.  

	View/Edit Details
	This link opens the appropriate page for viewing or editing (for Facility Action Required items only) information about a monitoring plan, test protocol, certification report, or emission report.  

Note:  The items under DEP Action Required display a View Details link because you may not edit any items requiring DEP action.

	Send Message
	This link opens the CEMDPS Correspondence page and allows you to send a message to another CEMDPS user.

Note:  The CEMDPS correspondence system is unavailable in the CEMDPS disconnected client application.

	View All Messages
	This link opens the Messages page, which displays all messages you have received.

Note:  The CEMDPS correspondence system is unavailable in the CEMDPS disconnected client application.

	View History
	This link opens the Work Item Assignment Report page, which shows the history of a monitoring plan, test protocol, certification report, or emission report.

	Remove <Item>
	This link appears for items under Facility Action Required only and allows you to delete the monitoring plan, test protocol, certification report, or emission report. Clicking this link opens the Delete <Item> page, which allows you to confirm or cancel the deletion.

Note:  The items under DEP Action Required do not have the Remove <Item> link because you may not edit or remove any items requiring DEP action.

	Replace with EDR Upload
	This link appears for Monitoring Plans and Test Protocols in the Facility Action Required section.  It opens the Monitoring Plan Upload or Test Protocol Upload page and allows you to upload an EDR file to replace the monitoring plan or test protocol.


Note:  The View/Edit Details (or View Details), Send Message, View All Messages, and View History options appear under every monitoring plan, test protocol, test report, and emission report listed in the Active Processes area.
Configuration Information

When you expand (+) the Configuration Information heading, summary information displays about the source combinations defined at your facility.  Each source combination name appears in a blue bar, along with the corresponding source combination ID.  The table below describes the data displayed for each source combination.

[image: image12.jpg]B Configuration Information
View Full Configuration

[Onit 12 (SCID: 601)
cemsip Emission Result Tvwe Sttus
oot o< sE PRIMARY Certited on 021182004
oz MO hsE BackwP Certifeton 02112004
e MO bsE PRIMARY Unceried
o MO hsE BackwP Unceriea
[Unit 13 (SCID: 602)
Cemsip Emission Result Tvwe Sttus
B paciy % PRIMARY Uncertiea
a2 opaciy % BackwP Unceriea





	Field
	Description

	View Full Configuration
	Clicking this link takes you to the Facility Configuration page, which displays detailed information about all phases of the facility configuration. 

	CEMSID
	Displays the CEMS ID for each CEMS associated with a source combination.

	Emission Result
	Displays the Emission Result the CEMS is associated with.

	Type
	Indicates whether the CEMS is the Primary CEMS or a Backup or Standby.

	Status
	Indicates the current status of the CEMS.


Delete <Item> Page

Whenever you click a link or button to remove an item in the CEMDPS, the Delete <Item> page displays asking if you are sure you want to delete the item. For example, if you click the Remove Test Protocol link for Test Protocol 123 in the Facility home page, the Delete Test Protocol page displays and asks, "Are you sure you want to remove Test Protocol 123?"  

Click the Yes button to delete the item, and click No to cancel the deletion.
[image: image13.jpg]r}ommnnweann}mmymm-
ent of Environmental Protection P
Bureau of Air Quality

Home ~~> Delee Monforing Plan

Delete Monitoring Plan

Conespondence

- Send Message
- View AllMessages

FrrETe
rrom nsen

o ExtuseR
oz 0mm0
rrom ns

o ExtuseR

his 5 3 ongersubject

Are you sure you want to remove Monitoring Plan 120

P Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (T17) 7053768
between the hours of £:00 AM to 430 PM or send an e-mailto
ep-efactshelpdeskteam@state.pa.us.





Download Synchronization Files

Occasionally, there may be users who want to work on CEMDPS projects offline instead of connecting to the online CEMDPS application.  These people use a disconnected CEMDPS client application and later upload their data to the online CEMDPS application.
Note:  For information on acquiring the CEMDPS disconnected client application, go to the DEP CEMS Website at: http://www.dep.state.pa.us/dep/deputate/airwaste/aq/cemspage/cems.htm.

The Download Synchronization Files page allows people using the disconnected client application to download the latest internal DEP codes file and configuration file for use in the offline application. Descriptions of the page's options appear below. 

Note:  Users who work in the online CEMDPS application do not need to download any files. Only people working offline using the CEMDPS disconnected client application need to download the files available from this page.  

[image: image14.jpg]r}ommnnweann}mmymm-
ent of Environmental Protection P

Bureau of Air Quality

- Send Message
- View AllMessages

| 2008-11-27 0000000
| From WTUSER

To: EXTUSER
|2008-11-27 0000000
From: NTUSER

To: EXTUSER

his 5 3 ongersubject

Horme -->Downisad Synchronization Fies

Download Synchronization Files

Contiguration Synchronization Fle
Internal DEP Cotes Synchrorization Fil

P Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (T17) 7053768
between the hours of £:00 AM to 430 PM or send an e-mailto
ep-efactshelpdeskteam@state.pa.us.





	Link
	Description

	Configuration Synchronization File
	Clicking this link opens the File Download dialog and allows users to save the file containing their most current facility configuration.  

Note:  Only people using the CEMDPS disconnected client application need to download this file.

	Internal DEP Codes Synchronization File
	Clicking this link opens the File Download dialog and allows users to save the file containing the current list of DEP's internal codes.

Note:  Only people using the CEMDPS disconnected client application need to download this file.


 XE "Work Item Type " \* MERGEFORMAT 

 XE "Work Item ID " \* MERGEFORMAT 

 XE "Work Item Assignment Report " \* MERGEFORMAT 

 XE "Updated By " \* MERGEFORMAT 

 XE "Status Date " \* MERGEFORMAT 

 XE "Status " \* MERGEFORMAT 

 XE "Last Update " \* MERGEFORMAT 

 XE "Due Date " \* MERGEFORMAT 

 XE "Comments " \* MERGEFORMAT 

 XE "Assigned To " \* MERGEFORMAT 

 XE "Assigned Date " \* MERGEFORMAT Work Item Assignment Report

The Work Item Assignment Report page displays a history of actions performed on a work item.  Information displayed and options available on this page appear in the table below.

[image: image15.jpg]Commonwealth of Pennsylvania [

ent of Environmental Protection P
g Bureau of Air Quality

Home

Work ltem Assignment Report

Work tem it 96

Work tem Type: Monitoring Plan

Commerts: recert source combo Unit 12 - alidated
s A0 LastUpdate _Updated By _ Status__ Status Date _ AssignedDate _ Assigned To__Due Date
— hox 07020007 temal User  Approved 0722007 070202007
T 05202007 temalUser  approved 06292007 08232007
| From EXTUSER 08282007 itemnal user _ approved _osap007_ osaro0r

| From: EXTUSER

.

=
| From: EXTUSER

i

A Dept. of Enviranmantal Protection DEP Home | CEM Home | Contacts | Help | Logout]

For assistance, please call DEP at (717) 705-3768
between the hours of £:00 AM to 430 PM or send an e-mail to
ep-efactshelpdeskteam@state. pa.us.





	Column
	Description

	Work Item Id
	Displays the unique identifier of the work item.

	Work Item Type
	Displays the type of work item.

	Comments
	Displays any comments entered about the work item.

	Last Update
	Displays the date the work item was last updated.

	Updated By
	Displays the user who updated the work item.

	Status
	Displays the work item's status.

	Status Date
	Displays the status date.

	Assigned Date
	Displays the date the work item was assigned.

	Assigned To
	Displays the user to whom the work item was assigned.

	Due Date
	Displays the date that action on the work item is due.


Upload EDR Submittal Packet

 XE "Monitoring Plan EDR File " \* MERGEFORMAT Monitoring Plan Upload

The Monitoring Plan Upload page lets you upload a monitoring plan file to the CEMDPS if your facility does not perform all continuous emission reporting processes using the CEMDPS online data entry screens.  When you upload a monitoring plan EDR file, the information in the file is loaded into the CEMDPS database and is then available to view, edit, and submit from the CEMDPS online interface.  After you upload all necessary EDR files for your monitoring plan, you must still validate the data and submit the monitoring plan to the DEP in the online interface.  (Please see Monitoring Plan Page for more information about validating and submitting monitoring plan data.)

To upload a monitoring plan, follow the instructions for each field, as listed below. 

[image: image16.jpg]C‘ommnwweanhﬁmm‘ylvlnl-
partment of Environmental Protection P
~ Bureau of Air Quality

Correspondence

- Send Message
- View AllMessages

FrrETe
rrom nsen

o ExtuseR
oz 0mm0
rrom ns

o ExtuseR

his 5 3 ongersubject

Home ~~>Manitaring Plan Uload

Monitoring Plan Upload

P Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (T17) 7053768
between the hours of £:00 AM to 430 PM or send an e-mailto
ep-efactshelpdeskteam@state.pa.us.





	Field Label
	Activity

	Monitoring Plan EDR File
	Click the Browse button to select a monitoring plan file to upload. This file must be a fixed length text file and must be in the correct layout for the EDR you are uploading based on the current Continuous Source Monitoring Manual. The file you choose displays in the text box.  


	Button
	Description

	Upload
	Clicking Upload uploads the data from the EDR file into the CEMDPS database.  The information is then available to view, edit, and submit from the CEMDPS online interface.


Notes:

· The EDR files you upload must be fixed length text files and must be in the correct layout for the EDR you are uploading based on the current Continuous Source Monitoring Manual.

· After you upload all necessary EDR files for your monitoring plan, you must still validate the data and submit the monitoring plan to the DEP in the online interface. (Please see Monitoring Plan Page for more information about validating and submitting monitoring plan data.)

Successful Upload

If the EDR text file layout is correct and all the data elements in the file are entered and formatted correctly, then the Monitoring Plan Upload page displays a confirmation message that the file uploaded successfully.

[image: image17.jpg]C‘ommnwweanhﬁmm‘ylvlnl-
partment of Environmental Protection P

~ Bureau of Air Quality

- Send Message
- View AllMessages

| 2006-11-27 om.0m008
 From: NTUSER

To: EXTUSER
|205-1127 000000

From: INTUSER.

To: EXTUSER

his 5 3 ongersubject

Home ~~>Moritoring Plan EDR Upload

Monitoring Plan EDR Upload

ng Plan Uploaded Successful

Monitori

P Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (T17) 7053768
between the hours of £:00 AM to 430 PM or send an e-mailto
ep-efactshelpdeskteam@state.pa.us.





When an EDR is uploaded to the CEMDPS, you can view and edit the new monitoring plan information from the Facility Action Required area of the Facility home page.  

Note:  After you upload all necessary EDR files for your monitoring plan, you must still validate the data and submit the monitoring plan to the DEP in the online interface.  (Please see Monitoring Plan Page for more information about validating and submitting monitoring plan data.)

The View/Edit Details Button

If your monitoring plan file uploads successfully, the View/Edit Details button displays.  Clicking this button allows you to view the uploaded EDR information in the CEMDPS's online interface. 

Errors During Upload

If there are problems with the EDR text file layout or data elements in the file, then the Monitoring Plan Upload page displays a list of errors you must fix in order for the file to upload successfully.

[image: image18.jpg]CEMDPS

Commonwealth of Pennsylvania
‘Department of Environmental Protection
‘L Bureau of Air Quality

~Home
- Create Synchvorization Files

Correspondence

- Send Message

- View allMessages
Inbox

2008-11-27 00:00:000

From: INTUSER

To: EXTUSER

2008-11-27 00:00:000

From: INTUSER

To: EXTUSER

| s 3longer subjet

Horme ~~>Moritoring Plan EDR Upload

Monitoring Plan EDR Upload

Error Valida ing Plan

Record Type Code: 312
Lines 1

1280 Alnital Submittal 20070405E0009110011111XXXX Combination 65-XXX-45 tons/day
1A TManufacturers Rating

Error: From Position 8 to § which represents "Change Flag” Cannot be null

Record Type Code: 812
Lines 1

12 8.0 Alnitial Submittal 20070405E0009:110011111XXXX Combination 65-XXX-45 tons/day
LA Manufacturer’s Rating

Error: From Position 59 to 66 which represents "Effective Date of InformationIs not a valid date.

Record Type Code: 312
Line 1

1250 Alnitial Submittal 20070405E00094110011111X0XXX Combination 65-XXX-45 tons/day
A ATManufacturer’s Rating

Error: From Position 63 to T2 which represents "DEP Facility ID Code" should be an llumber

Record Type Code: 812
Linez 1

12,0 Alnitial Submittal 20070405E00094110011111XXXX Combination 65-XXX-15 tons/day

AL ATManufacturers Rating

Error: From Position 74to 80 which represents "DEP Source Combination ID Code" should be an Humber

P4 Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (717) 7053768
between the hours of £:00 AM to 4:30 PM or send an e-mail to
ep-efactshelpdeskteam@state.pa.us.





Each error listed includes the Record Type Code for the EDR, the line number containing the error, the line of data containing the error, and a description of the error.  The description includes the field name and record position of the error, if applicable.  You can adjust your text file and try to upload it as often as necessary until all errors clear and the file uploads successfully.

 XE "Test Protocol File " \* MERGEFORMAT 

 XE "Cover Letter Statements and Signature File " \* MERGEFORMAT Test Protocol Upload

The Test Protocol Upload page lets you upload a test protocol file to the CEMDPS if your facility does not perform all continuous emission reporting processes using the CEMDPS online data entry screens. When you upload a test protocol EDR file, the information in the file is loaded into the CEMDPS database and is then available to view, edit, and submit from the CEMDPS online interface.  After you upload all necessary EDR files for your test protocol, you must still validate the data and submit the test protocol to the DEP in the online interface.  (Please see Test Protocol Page for more information about validating and submitting test protocol data.)

To upload a test protocol, follow the instructions for each field, as listed below. 

[image: image19.jpg]r}ommnnweann}mmymm-
ent of Environmental Protection P
Bureau of Air Quality

Home ~>Test Protacal Upload!

Test Protocol Upload

Conespondence

- Send Message
- View AllMessages

FrrETe
rrom nsen

o ExtuseR
oz 0mm0
rrom ns

o ExtuseR

his 5 3 ongersubject

P Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (T17) 7053768
between the hours of £:00 AM to 430 PM or send an e-mailto
ep-efactshelpdeskteam@state.pa.us.





	Field Label
	Activity

	Test Protocol File
	Click the Browse button to select a test protocol file to upload. This file must be a fixed length text file and must be in the correct layout for the EDR you are uploading based on the current Continuous Source Monitoring Manual. The file you choose displays in the text box.  

	Cover Letter Statements and Signature File
	Click the Browse button to select a cover letter and/or signature file to upload along with your test protocol.  This file may be in any format (*.pdf, *.doc, etc.).


	Button
	Description

	Upload
	Clicking Upload uploads the data from the EDR file into the CEMDPS database.  The information is then available to view, edit, and submit from the CEMDPS online interface.


Notes:

· The EDR files you upload must be fixed length text files and must be in the correct layout for the EDR you are uploading based on the current Continuous Source Monitoring Manual.

· After you upload all necessary EDR files for your monitoring plan, you must still validate the data and submit the test protocol to the DEP in the online interface. (Please see Test Protocol page for more information about validating and submitting test protocol data.)

Successful Upload

If the test protocol EDR text file layout is correct and all the data elements in the file are entered and formatted correctly, then the Test Protocol Upload page displays a confirmation message that the file uploaded successfully.

[image: image20.jpg]~ Commonwealth of Pennsylvania
ent of Environmental Protection I’
Bureau of Air Quality

- Send Message
- View AllMessages

2008-11-27 00:00:000
From: INTUSER

To: EXTUSER

20061127 0000000
From: NTUSER
To EXTUSER

his s 3 longersubect

Home ~->Test Protocol Lioad

Test Protocol Upload

Test Protocol Uploaded Successful

P Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout]

For assistance, please call DEP at (717) 7053768
between the hours of £:00 AM to 430 PM or send an e-mail to
ep-efactshelpdeskteam@state.pa.us.





When an EDR is uploaded to the CEMDPS, you can view and edit the new test protocol information from the Facility Action Required area of the Facility home page.  

Note:  After you upload all necessary EDR files for your test protocol, you must still validate the data and submit the test protocol to the DEP in the online interface.  (Please see Test Protocol page for more information about validating and submitting test protocol data.)

The View/Edit Details Button

If your test protocol file uploads successfully, the View/Edit Details button displays.  Clicking this button allows you to view the uploaded EDR information in the CEMDPS's online interface. 

Errors During Upload

If there are problems with the EDR text file layout or data elements in the file, then the Test Protocol Upload page displays a list of errors you must fix in order for the file to upload successfully.

[image: image21.jpg]‘E Commonwealth of Pennsylvania [
partment of Environmental Protection P

‘_ Bureau of Air Quality

Correspondence
- Send Message
- View AllMessages
Inbox
2008-11-27 00:00:000
From: INTUSER
To: EXTUSER
2008-11-27 00:00:000
From: INTUSER
To: EXTUSER

| s 3longer subject

Home ~~>Test Protacol Upload!

Test Protocol Upload

Error Validat

ng Test Protocol

Record Type Code: 303
Line 1

803 11.11100019200703049 James ISmith Dir ector of Testing ABC Testing Dear Mr. Smith: 333 Maple Street
Error: From Position 910 13 which represents “DEP Facilit ID Code” should be an lumber

Record Type Code: 303

Linez 1

803 11.11100019200703049 James ISmith Dir ctor of Testing ABC Testing Dear Mr. Smith: 333 Maple Street
rom Position 14to 21 which represents "Proposed Testing Date" Is not a valid date

P Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout]

For assistance, please call DEP at (T17) 7053768
between the hours of £:00 AM to 430 PM or send an e-mailto
ep-efactshelpdeskteam@state.pa.us.





Each error listed includes the Record Type Code for the EDR, the line number containing the error, the line of data containing the error, and a description of the error.  The description includes the field name and record position of the error, if applicable.  You can adjust your text file and try to upload it as often as necessary until all errors clear and the file uploads successfully.

 XE "Certification Reports File " \* MERGEFORMAT Certification Reports Upload

The Certification Reports Upload page lets you upload a certification report file to the CEMDPS if your facility does not perform all continuous emission reporting processes using the CEMDPS online data entry screens. When you upload a certification report EDR file, the information in the file is loaded into the CEMDPS database and is then available to view, edit, and submit from the CEMDPS online interface.  After you upload all necessary EDR files for your certification report, you must still validate the data and submit the certification report to the DEP in the online interface.  (Please see Certification Report page for more information about validating and submitting certification report data.)

To upload a certification report, follow the instructions for each field, as listed below. 

[image: image22.jpg]Commonwealth of Pennsylvania =
ent of Environmental Protection I’

Bureau of Air Quality R

Home ~->Cerifcatian Reports Uploac!

Certification Reports Upload

Conespondence

- Send Message
- View AllMessages

2008-11-27 00:00:000
From: INTUSER

To: EXTUSER

2008-11-27 00:00:000

From: INTUSER.

To: EXTUSER

his 5 3 ongersubject

P Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (T17) 7053768
between the hours of £:00 AM to 430 PM or send an e-mailto
ep-efactshelpdeskteam@state.pa.us.





	Field Label
	Activity

	Certification Reports File
	Click the Browse button to select a certification report file to upload. This file must be a fixed length text file and must be in the correct layout for the EDR you are uploading based on the current Continuous Source Monitoring Manual. The file you choose displays in the text box.  


	Button
	Description

	Upload
	Clicking Upload uploads the data from the EDR file into the CEMDPS database.  The information is then available to view, edit, and submit from the CEMDPS online interface.


Notes:

· The EDR files you upload must be fixed length text files and must be in the correct layout for the EDR you are uploading based on the current Continuous Source Monitoring Manual.

· After you upload all necessary EDR files for your certification report, you must still validate the data and submit the certification report to the DEP in the online interface. (Please see Certification Report Page for more information about validating and submitting certification report data.)

Successful Upload

If the certification report EDR text file layout is correct and all the data elements in the file are entered and formatted correctly, then the Certification Reports Upload page displays a confirmation message that the file uploaded successfully.

[image: image23.jpg]Commonwealth of Pennsylvania
® ent of Environmental Protection
3 Bureau of Air Quality

-

=

- Send Message
- View AllMessages

2008-11-27 00:00:000

From: INTUSER.

To: EXTUSER

| 2006-11.27 om0m000

From: INTUSER.

To: EXTUSER

his s 3 longersubjct

Home ~-> Certiication Report Uploa

Certification Report Upload

Certification Report Uploaded Successfully

P Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout]

For assistance, please call DEP at (T17) 7053768
between the hours of £:00 AM to 4:30 PM or send an e-mailto
ep-efactshelpdeskteam@state.pa.





When an EDR is uploaded to the CEMDPS, you can view and edit the new certification report information from the Facility Action Required area of the Facility home page.  

Note:  After you upload all necessary EDR files for your certification report, you must still validate the data and submit the certification report to the DEP in the online interface.  (Please see Certification/Test Report page for more information about validating and submitting certification report data.)

The View Submittal Button

If your certification report file uploads successfully, the View Submittal button displays.  Clicking this button allows you to view or save a document in PDF format that contains all certification report information to be submitted to the DEP.  

Note:  You must have Adobe® Acrobat in order to view the PDF document generated from the View Submittal button.

Errors During Upload

If there are problems with the EDR text file layout or data elements in the file, then the Certification Reports Upload page displays a list of errors you must fix in order for the file to upload successfully.

Each error listed includes the Record Type Code for the EDR, the line number containing the error, the line of data containing the error, and a description of the error.  The description includes the field name and record position of the error, if applicable.  You can adjust your text file and try to upload it as often as necessary until all errors clear and the file uploads successfully.

 XE "Quarterly Reports File " \* MERGEFORMAT 

 XE "Is this a Sample Report? " \* MERGEFORMAT 

 XE "Cover Letter Statements and Signature File " \* MERGEFORMAT Quarterly Reports Upload

The Quarterly Reports Upload page lets you upload a quarterly report file to the CEMDPS and include cover letters and signature files with the report.  Also, you may indicate whether the report is a sample.

To upload a quarterly report, follow the instructions for each field, as listed below.  

[image: image24.jpg]Commonwealth of Pennsylvania

EMDPS ent of Environmental Protection i

> Bureau of Air Quality

Horme ~->Cuarterly Reports Upload

Quarterly Reports Upload

- View AllVessages Cover Latter

O e || S

Inbox Signeture Flle

e —
From wTUSER i

7o ExtuseR EE) 1

o I tis o Sample

| Report?
A A Istis an icicator

From: INTUSER. Report?
To: EXTUSER

| 2006-11-27 om.0m008

Valiate Only

his 5 3 ongersubject

Eission Resuts ars currently undergoing certifiation and have yet1o be
approved Please confitmthat the data being submited for all Emission Resuts
mthe currently ceriied system and not from the change system

Yes, confirn

A Dept. of Enviranmantal Protection DEP Home | CEM Home | Contacts | Help | Logout]

For assistance, please call DEP at (717) 7053768
between the hours of £:00 AM to 430 PM or send an e-mail to
ep-efactshelpdeskteam@state. pa.us.





	Field Label
	Activity

	Quarterly Reports File
	Click the Browse button to select a report file to upload. This file must be a fixed length text file and must be in the correct layout for the EDR you are uploading based on the current Continuous Source Monitoring Manual. The file you choose displays in the text box.  

	Cover Letter Statements and Signature File
	Click the Browse button to select a cover letter and/or signature file to upload along with your quarterly report. This file may be in any format (*.pdf, *.doc, etc.).

	PostMark Date
	Enter the postmark date of the information in mm/dd/yyyy format or click the calendar icon to select a date from a calendar.  (See Date Selection for information on using the calendar to choose a date.)

Note:  This option only appears for DEP users with a "Super User" designation.  It offers the opportunity for DEP personnel to enter a post mark date for reports they receive on CD or another source that they must upload to the CEMDPS themselves.

	Comments
	Enter comments about the quarterly report.

	Is this a Sample Report?
	Click to place a checkmark in the checkbox if your quarterly report is a sample report. 

	Is this an Indicator Report?
	Click to place a checkmark in the checkbox if your report is an indicator report.

	Validate Only
	Click to place a checkmark in the checkbox if you want to validate the upload only.  Even if the report is validated, you will not have the option to submit the report if you check this option.  See Successful Upload using the Validate Only Option for more information.

	Yes, I confirm
	The DEP requires that the report information provided is for currently certified emission results.  Click the Yes, I confirm checkbox to indicate that this is true.  

Note: The Upload button is only available when the Yes, I confirm checkbox is checked.


	Button
	Description

	Upload
	Clicking Upload uploads the data from the EDR file into the CEMDPS database.  


Successful Upload using the Validate Only Option

If you check the Validate Only option when uploading a report and if the quarterly report text file layout is correct and all the data elements in the file are formatted correctly, then the Quarterly Reports Upload Results page displays a confirmation message that the file was validated successfully.  The results page also displays any warnings about missing information in the quarterly report.  At this point, the quarterly report has not been submitted to the DEP.  The Validate Only option does not offer the opportunity to submit the report to the DEP after successful validation.
[image: image25.jpg]Commonwealth of Pennsylvania \
ent of Environmental Protection T
‘. Bureau of Air Quality

Home ~->Cuarterly Reports Upload

Quarterly Reports Upload Result

Correspondence

- Send Message

- View AllMessages
Inbox

2008-11-27 00:00:000

From: INTUSER

To: EXTUSER

2008-11-27 00:00:000

From: INTUSER.

To: EXTUSER

his 5 3 ongersubject

Quarterly Report was Validated Successfull

Work tem o

Emission Reportld 0

|| Postmark Date: 077312007
Caver Letter
Sttemerts And  View Fll
Signature File
Commerts
Sample Report? o
ndicator Report? 1o

Fil HasWarnings?  Ves

WARNINIGS GENERATED BY THE SYSTEM

888 record not submitted for analyz
analyzer

777, Emission Resultid:2609 reported through 830 refers to this

888 record not submitted for analyz
analyzer

8, Emission Resutid

609 reported through 880 refers to this

888 record not submitted for analyzer 5755, Emission Resultid:2609 reported through 580 refers to
this analyzer

P4 Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (T17) 7053768
between the hours of £:00 AM to 430 PM or send an e-mail to
ep-efactshelpdeskteam@state. pa.us.





Successful Upload

If the quarterly report text file layout is correct and all the data elements in the file are formatted correctly, then the Quarterly Reports Upload Results page displays a confirmation message that the file was validated successfully.  The results page also displays any warnings about missing information in the quarterly report.  Finally, the page warns that the DEP can reject your submittal based on the system generated warnings shown, and asks you to confirm this before submitting to DEP.

[image: image26.jpg]Commonwealth of Pennsylvania \
ent of Environmental Protection T
‘. Bureau of Air Quality

Home ~->Cuarterly Reports Upload

Quarterly Reports Upload Result

Correspondence

- Send Message

- View AllMessages
Inbox

2008-11-27 00:00:000

From: INTUSER

To: EXTUSER

2008-11-27 00:00:000

From: INTUSER.

To: EXTUSER

his 5 3 ongersubject

|| Quarterly Report was Validated Successfully
Work tem 1523

EmissionReportid 1895

|| Postmark Date: 077312007
Caver Letter
Sttemerts And  View Fll
Signature File
Commerts
Sample Report? o
ndicator Report? 1o

Fil HasWarnings?  Ves

WARNINIGS GENERATED BY THE SYSTEM

888 record not submitted for analyz
analyzer

771, Emission Resultd:2609 reported through 880 refers to this

888 record not submitted for analyz
analyzer

8, Emission Resultid:2609 reported through 580 refers to this.

888 record not submitted for analyzer 5755, Emission Resultid:2609 reported through 580 refers to
this analyzer

DEP con refect your subritta based on the warnings generatec! by the system
Please acknowledgs that you are aware of the warfings

Yes)do

Vi Sutmital

P4 Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|





Note:  The CEMDPS system provides screens for entering or editing data for all continuous emission reporting except for quarterly reports.  Quarterly reports must be uploaded as a file and are never available for editing in the online interface as are other processes (monitoring plans, test protocols, certification reports).

The View Submittal Button

If your quarterly report file uploads successfully, the View Submittal button displays.  Clicking this button allows you to view or save a document in PDF format that contains all quarterly report information submitted to the DEP.  

Note:  You must have Adobe® Acrobat in order to view the PDF document generated from the View Submittal button.

The Submit Button

If your quarterly report file is validated and you click to check the Yes, I do check box to acknowledge that the DEP may reject your report submission based on the displayed system warnings, the Submit button becomes available and allows you to submit your report to the DEP for review.

Errors During Upload

If there are problems with the text file layout or data elements in the file, then the Quarterly Reports Upload page displays a list of errors you must fix in order for the file to upload successfully.

[image: image27.jpg]Commonwealth of Pennsylvania
ent of Environmental Protection ¥
Bureau of Air Quality

[ comespondence |

Horme ~->Cuarterly Reports Upload

Quarterly Reports Upload

Ervor Validat

ng Quarterly Report

- Send Message
- View AllMessages

| 2006-11-27 om.0m008
[ From:
To:

| 20061127 smon0n0
From

To:

his 5 3 longersubject

Record Type Code: null
Line 1

Line Data: 123456

Error: Invalid Record Type Code.

P Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (T17) 7053768
between the hours of £:00 AM to 430 PM or send an e-mailto
ep-efactshelpdeskteam@state.pa.





Each error listed includes the Record Type Code for the EDR, the line number containing the error, the line of data containing the error, and a description of the error.  The description includes the field name and record position of the error, if applicable.  You can adjust your text file and try to upload it as often as necessary until all errors clear and the file uploads successfully.

Facility Configuration

 XE "Units " \* MERGEFORMAT 

 XE "Type " \* MERGEFORMAT 

 XE "Status " \* MERGEFORMAT 

 XE "Revision # " \* MERGEFORMAT 

 XE "Primary Facility Id " \* MERGEFORMAT 

 XE "Phase 3 Approved " \* MERGEFORMAT 

 XE "Phase 1 Submitted " \* MERGEFORMAT 

 XE "Parameter " \* MERGEFORMAT 

 XE "Monitoring Point Code " \* MERGEFORMAT 

 XE "ID " \* MERGEFORMAT 

 XE "Facility Name " \* MERGEFORMAT 

 XE "Facility Configuration " \* MERGEFORMAT 

 XE "Corrected To " \* MERGEFORMAT 

 XE "Configuration Filter " \* MERGEFORMAT 

 XE "Company Name " \* MERGEFORMAT 

 XE "CEMS Type " \* MERGEFORMAT 

 XE "Basis of Measurement " \* MERGEFORMAT Facility Configuration

The Facility Configuration page displays information about all phases of a facility's configuration.  In addition, you can choose to view just those items that are in a particular phase or view more details about one item in particular.  Descriptions of the Facility Configuration page's structure and options appear below. 

[image: image28.jpg][(EEMDPS

T
B

Commonwealth of Pennsylvania
Department of Environmental Protection P

Bureau of Air Quality

Quick Links.

~Home
- Creste Synchronizaton Fies

Correspondence
- Send Message
- View &llMessages
Inbox
2008-11-27 00:00:000
From: INTUSER
To: EXTUSER
2008-11-27 00:00:000
From: INTUSER
To: EXTUSER

his 5 3 longersubect

Home ~-> View Facilty Configuration

Basic Information
Primary Facilty : $10331

Company Name:  CASTLE RUBBER LLC
FacityName:  CASTLE RUBBER LLCEAST BUTLER BORO

Fa

cility Configuration

Configuration Fitter: [All Phases. =] [aeoy |

Unit 12 (ID: 6001) [VEw |

el [ T ] =i i s it Mt e | o e
T e or | sas actve

| VIEW || cEms {18001 1 PRMARY | |Approved] 0211872004

[Uew | covs froooz] 1 [meciae [aperoved oanaros
e ]| covs fios] 1 prmeary] [aperoved
v ]| cos fiozs] 1 [macke [aperaved

Unit 13 (ID: 6002) [VEw |

Tre O O pametr e S Cod WD ot ST e
iew JFssenion coz  [psmen nactve
[Vew | cows fiozo] 1 prmeary] [aperaved
v ]| covs o271 [macke [aperoved

P4 Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (717) 7053768
between the hours of £:00 AM to 4:30 PM or send an e-mail to
ep-efactshelpdeskteam@state.pa.us.





Basic Information

The Basic Information section displays three pieces of information about the facility: the primary facility ID, the company name, and the facility name.

Configuration Filter

The Configuration Filter drop-down allows you to choose the CEMSs shown in the source combination tables beneath the filter based on the CEMS's phase in the submittal process.  

	Field Label
	Description

	Configuration Filter
	Provides a drop-down to choose a process phase:  Certified, Certified and In-process, In-process, or All Phases.  All CEMSs in the configuration that are currently in that phase appear in the source combination tables beneath the filter drop-down.  The default view is to show CEMSs from all phases.


	Button
	Description

	Apply
	Click Apply to update the source combination tables to show only those CEMSs that are currently in the phase selected in the Configuration Filter drop-down.


To change the configuration view using the Configuration Filter:

1. Use the Configuration Filter drop-down to select a CEMS phase (Certified, Certified and In-process, In-process, or All Phases).

2. Click Apply. All CEMSs in the facility's configuration that are currently in the phase selected in the Configuration Filter appear in the source combination tables.

Source Combination Tables

The source combination tables display information about source combinations in the facility's configuration and allow you to view more details about a source combination and its components.

	Column
	Description

	Source Combination Name (ID)
	For each source combination, the combination name and ID appear in the first row of the table.

	Type
	Indicates the type of component of the source combination.

	ID
	Displays the unique identifier of the component of the source combination.

	Revision #
	Indicates the continuous source monitoring manual revision number of the CEMS.

	CEMS Type
	Indicates the type of CEMS (Primary, Backup, or Standby).

	Parameter
	Displays the parameter/pollutant for the emission result or analyzer.

	Units
	Indicates the units of measurement of the emission result or analyzer.

	Basis of Measurement
	Indicates the basis of measurement of the emission result or analyzer.

	Corrected To
	Displays the corrected to value of the emission result.

	Monitoring Point Code
	Indicates the monitoring point code of the analyzer.

	Status
	Displays the current status of the component.

	Phase 1 Submitted
	Displays the date of Phase 1 submission.

	Phase 3 Approved
	Displays the date of Phase 3 approval.


	Button
	Description

	View
	Clicking the View button next to a source combination or component takes you to a page with more detailed information about that item. For more information, see the following pages:

· View Source Combination
· View Emission Result
· View CEMS
· View Analyzer


 XE "View Source Combination " \* MERGEFORMAT 

 XE "Units " \* MERGEFORMAT 

 XE "Status " \* MERGEFORMAT 

 XE "Rated Capacity " \* MERGEFORMAT 

 XE "Plan Approval Number " \* MERGEFORMAT 

 XE "Parameter " \* MERGEFORMAT 

 XE "ID " \* MERGEFORMAT 

 XE "DEP ID " \* MERGEFORMAT 

 XE "Corrected To " \* MERGEFORMAT 

 XE "Capacity Information Source " \* MERGEFORMAT 

 XE "Basis of Measurement " \* MERGEFORMAT View Source Combination

The View Source Combination page displays detailed information about a source combination at a facility.  From this page, you can also view details about other components of the source combination.  Information about the structure and options available on this page appear in the following sections.

[image: image29.jpg]Commonwealth of Pennsylvania

CEMDPS :mnn of Environmental Protection 3

Bureau of Air Quality

Home ~-> View Facilty Configuration ~-> Visw Saurce Combination

~Home . _
View Source Combination

Kiln 5

Correspondence
- Send Message
- View AllVessages 6003

Inbox Plan Approval Number: 48.993-40
e P Rted Capacty: 1000 MBtuhY

From: INTUSER. eyt

Recards of Manufacturer
To: EXTUSER

koo General Informati
2006-11-27 0000000 Ecuivalent iameter of

From: NTUSER the flue ot the

e monitorng system 7 feet

measuremert location
his 5 3 longersubjct s

Type of nearest
upstream dsturbance:
Distance of nearest 7 feet

upstream disturbance
toMSHL:

et

Type of nearest
downstream Fan
disturbance:

Distance of nearest 7 fest
downstream
disturbance o MSML:

Type of nearest
pollton cortrol cycione
ectipment;

Distance of nearest 7 feet
polltion cortrol

ectipment to MSML:

Location of poltion
controlecuipmert D
reative o MSML:
Distance of enission 7 feet
pairt f manioring
gases to MSML

Distance of flue walls 7 feet
from sample

acauistion point:

Commerts: Commerts General 278

Ecqivalent diameter of
the flue ot the

montoring system 7 feet
measuremert location
sy

Type of nearest
upstream disturbance:
Distance of nearest 7 feet

upstream dsturbance
toMSHL:

it

Type of nearest
downstream Fan
disturbance:

Distance of nearest 7 feat
downstream
disturbance to MSML:

Type of nearest
pollton cortrol Cycione

ectipment:

Distance of nearest 7 feet

pollton cortrol

ectipment to MSML:

Location of poltion

controlequipmert D

elative to MSHL:

Distance of enission 7 feet

pairt f manitoring

gases to MSML

Distance of flue walls 7 feet

from sample

acauistion poirt:

Commerts: Commerts General 278

Emission Results

Basis of
n Paameter s Bsie el CorrectedTo  Status.

10023 Opacty % i & active

A Dept. of Enviranmantal Protection DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (717) 705.3768
between the hours of £:00 AM to 430 PM or send an e-mail to
ep-efactshelpdeskteam@state. pa.us.





Basic Information/General Information

The Basic Information and General Information sections provide an overall description of the source combination.

Emission Results

The Emission Results section lists the emission results associated with the source combination and allows you to view more details about each emission result.

	Column
	Description

	ID
	Displays the emission result ID.

	Parameter
	Displays the parameter/pollutant for the emission result.

	Units
	Indicates the units of measurement of the emission result.

	Basis of Measurement
	Indicates the basis of measurement of the emission result.

	Corrected To
	Displays the corrected to value of the emission result.

	Status
	Displays the status of the emission result.


	Button
	Description

	[image: image30.jpg]



	Clicking View next to an emission result displays the View Emission Result page, which contains detailed information about the emission result.


 XE "View Emission Result " \* MERGEFORMAT 

 XE "Variable Emission Result ID Code " \* MERGEFORMAT 

 XE "Truncation Level " \* MERGEFORMAT 

 XE "Status " \* MERGEFORMAT 

 XE "Start Date " \* MERGEFORMAT 

 XE "Revision # " \* MERGEFORMAT 

 XE "Regulatory Citation " \* MERGEFORMAT 

 XE "Reason for Installation " \* MERGEFORMAT 

 XE "Phase 3 Approved " \* MERGEFORMAT 

 XE "Phase 1 Submitted " \* MERGEFORMAT 

 XE "Penalty Parameter " \* MERGEFORMAT 

 XE "Or'd Emission Standard ID Code " \* MERGEFORMAT 

 XE "Or'd Emission Result ID Code " \* MERGEFORMAT 

 XE "ID " \* MERGEFORMAT 

 XE "End Date " \* MERGEFORMAT 

 XE "Emission Standard Value " \* MERGEFORMAT 

 XE "Emission Standard for Or'd Standard " \* MERGEFORMAT 

 XE "Emission Standard Direction " \* MERGEFORMAT 

 XE "Emission Standard " \* MERGEFORMAT 

 XE "Data Availability Standard for Or'd Standard " \* MERGEFORMAT 

 XE "Data Availability Standard " \* MERGEFORMAT 

 XE "CEMS Type " \* MERGEFORMAT 

 XE "And/Or Standard (for or'd Standards) " \* MERGEFORMAT 

 XE "And/Or Flag (for "or'd" Standards) " \* MERGEFORMAT View Emission Result

The View Emission Result page displays detailed information about an emission result at a facility.  From this page, you can also view details about the source combination and the CEMSs associated with the emission result.  Information about the structure and options available on this page appear in the following sections.

[image: image31.jpg]‘ Bureau of Air Quality

C of i
ICEMDPS e T ;

Quick Links.

| “Home
- Creste Synchvonizefion Fes

Correspondence

- Send Message

- View AllMessages
Inbox

2008-11-27 00:00:000

From: INTUSER

To: EXTUSER

2008-11-27 00:00:000

From: INTUSER.

To: EXTUSER

his 5 3 ongersubject

Home ~-» View Facilty Configuration - View Emission Resut

Basi
[——— |
e o0z
e o essuemert
coneetea T B
Dt
Rered
Reasons
Remson for stalation Reuistory Caton

Poan spprova Craont
En ion Standards

P Anaor o ora
erssion o Emission Truncation_penatty Tag  Emission Emission
Standara SIS g Standard poC L sandard T eter o "or” ResutlD Standara

Code Standards)  Code D Cods

o
v,
o

Data Availability Standards

AndOr Standard | EMiSsion  Data Availabilty|

bt Avatabity Ena Eission M0 S Stndard Standara
Sandard SR e stiwa SO0 Goora tarora
Standarc:___Standara
o e
e waoanr
CEMS
Pzt Phased
D Reveions  cEMsTpe  swws  wenel  Phased
e ] v 1 R woed  memn omnsmon

P4 Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (717) 7053768
between the hours of £:00 AM to 430 PM or send an e-mail to
ep-efactshelpdeskteam@state. pa.us.





Basic Information

The Basic Information section displays five pieces of information about the emission result, as shown in the following table.

	Field Label
	Description

	Source Combination
	Indicates the source combination to which the emission result belongs.

	DEP ID
	Indicates the DEP ID of the emission result.

	Basis of Measurement
	Displays the Basis of Measurement for the emission result. Examples of possible values are:

· Wet (W)

· Dry (D)

· Not Applicable (N)

	Corrected To
	Displays the Corrected To value for the emission result. Examples of possible values are:

· **  (Not Applicable)

· 0% O2

· 10% O2

· 12% O2

· 15% O2

· 7% O2

· 8% O2

	Data Substitution Required
	Indicates whether data substitution is required (Yes or No).


	Button
	Description

	[image: image32.jpg]



	Clicking this button displays opens the View Source Combination page with more details about the source combination.


Reasons

This section displays the emission result reasons for the emission result, as described in the following table.

	Column
	Description

	Reason for Installation
	Displays the Reason for Installation. Examples of possible values are:

· Not Applicable

· Unknown

· NESHAPS

· NSPS

· Department Order

· Acid Rain Phase I

· Acid Rain Phase II

· Plan Approval

· PSD

· RACT

· SIP

· Trading Program

	Regulatory Citation
	Displays the regulatory citation for the reason represented by the Reason for Installation (for instance, 25 PA Code - Chapter 127, 25 PA Code Chapter 145, etc.).


Emission Standards

This section displays emission standards associated with the emission result, as shown in the table below.

	Column
	Description

	Emission Standard
	Displays the emission standard to identify the type of averaging/summation period involved. Examples of possible values are:

No ESIDC (Use for DA Std Only)

Std1dev, no exceptions

1-Minute average, 3 exceptions in hour

Std2dev, no exceptions

1-Minute average, block

4-hour average, block

1-day average, block

12-hour average, block

Daily averages, 2 exceptions in 30-day

24-hour average, rolling by 1 hour

30-day average, rolling by 1 day

6-minute average, block

1-hour average, block

1-day sum

4-day average, rolling by 1 day

12-month sum, rolling by 1 month

3-hour average, rolling by 1 hour

12-month average, rolling by 1 month

4-hour average, rolling by 1 hour

3-hour average, block

8-hour average, rolling by 1 hour

7-day average, rolling by 1 day

12-hour average, rolling by 1 hour

1-day average, block, geometric

1-Year sum

30-Operating-Day operating hour average, by 1 day

Std1dev, 3 exceptions in hour

1-month average, block



	Start Date
	Displays the starting date the standard applies in mm/dd/yyyy format or click the calendar icon to select a date from a calendar.  (See Date Selection for information on using the calendar to choose a date.) 

	End Date
	Displays the last date the standard applies in mm/dd/yyyy format or click the calendar icon to select a date from a calendar.  (See Date Selection for information on using the calendar to choose a date.)  

	Emission Standard Value
	Displays the value of the emission standard.  If the emission result is subject to a variable standard (based on process operating conditions, etc.), leave this field blank.  Use format F16.6 for data entered in this field.

	Variable Emission Result ID Code
	Should the emission result be subject to a variable standard (based on process operating conditions, etc.), displays the DEP Emission Result ID Code for the emission result used to report such variable emission standard for comparison with the emission result represented by this record.  

	Emission Standard Direction
	Displays the Emission Standard Direction.  Acceptable values are:

Less Than 

Violation if monitoring result is less than the emission standard value

Less Than Equal

Violation if monitoring result is less than or equal to the emission standard value

Greater Than

Violation if monitoring result is greater than the emission standard value

Greater Than Equal

Violation if monitoring result is greater than or equal to the emission standard value



	Truncation Level
	Displays the truncation level (as supplied by the PADEP).  Acceptable values are in the range -6 to +9, with +0 as a valid value.

	Penalty Parameter
	Displays the Penalty Parameter. Examples of possible values are:

E-General 1-Month Ave

D-MWI Opacity

E-General 12-Month roll

E-Boiler/General 20% Standard Opacity

E-MWI CE

E-Boiler/General 60% Standard Opacity

D-Hospital Incinerator CE, CO, Temp.

E-Cement Kiln 20% Standard Opacity

D-MWI CE, CO, Temp.

E-Cement Kiln 60% Standard Opacity

E-Hospital Incinerator Daily CO

E-FCC 20% Standard Opacity

E-MWI 4 Day CO

E-FCC 60% Standard Opacity

E-MWI 4 Hour CO

E-FCC 20% Standard After October 2004 Opacity

E-MWI 8 Hour CO

E-FCC 60% Standard After October 2004 Opacity

E-MWI Daily CO

E-MWI 10% Standard Opacity

E-MWI Daily CO After ???

E-MWI 30% Standard Opacity

E-Interim Guidelines Hourly-Main Standards

E-MWI Daily SO2

E-MWI Daily HCl

E-MWI Hourly SO2

E-MWI Daily HCl After ???

E-Blr/G Daily (lbs/Mbtu, ppm, lbs/hr) SO2, NOx, CO

E-MWI Daily HCl no Reduction

E-Boiler/General 2-in-30 Day SO2, NOx, CO

E-Boiler Homer City Only NOx

E-Boiler/General 30-Day SO2, NOx, CO

E-MWI Daily NOx

E-Boiler/General Daily/30D (lbs/Mbtu) SO2, NOx, CO

D-Boiler/General Hourly Opacity

D-MWI SO2, NOx, HCl

D-Cement Kiln Opacity

D-Boiler/General Hourly, Daily SO2, NOx, TRS

D-FFC Opacity

E-Interim Guidelines Hourly - Temp. Adj Stds

D-FFC Opacity October 2004

E-MWI Minute Temp.



	And/Or Flag (for "or'd" Standards)
	If the emission standard applies in addition to any other emission standards (or is the only emission standard), displays And.  If the emission standard is one of a number of alternatives, displays Or.

	Or'd Emission Result ID Code
	If the emission standard is one of a number of alternatives, displays the emission result ID code to which the ord standard applies.  Otherwise, this field is blank.

	Or'd Emission Standard ID Code
	If the emission standard is one of a number of alternatives, displays the emission standard ID code of the emission result ID code for the ord standard which applies.  Otherwise, this field is blank.


Data Availability Standards

This section displays the data availability standards associated with the emission result, as shown in the following table.

	Column
	Description

	Data Availability Standard
	Displays the data availability standard. Examples of possible values are:

Value

Description

1

90% hours in month

2

95% hours in quarter

3

90% averages in month

4

75% averages in month

5

85% averages in quarter

6

100% hours in quarter

7

95% hours in day

8

50% hours in 30-day

9

23 days in 30-day

10

100% hours in day



	Start Date
	Displays the starting date the standard applies in mm/dd/yyyy format or click the calendar icon to select a date from a calendar.  (See Date Selection for information on using the calendar to choose a date.)

	End Date
	Displays the last date the standard applies in mm/dd/yyyy format or click the calendar icon to select a date from a calendar.  (See Date Selection for information on using the calendar to choose a date.) 

	Emission Standard
	Displays the emission standard.  If the Data Availability Standard is not related to an Emission standard, then No ESIDC (Use for DA Std Only) displays. Examples of possible values are:

Value

Description

0

No ESIDC (Use for DA Std Only)

1

1-Minute average, 3 exceptions in hour

2

1-Minute average, block

3

1-day average, block

4

Daily averages, 2 exceptions in 30-day

5

30-day average, rolling by 1 day

6

1-hour average, block

7

4-day average, rolling by 1 day

8

3-hour average, rolling by 1 hour

9

4-hour average, rolling by 1 hour

10

8-hour average, rolling by 1 hour

11

12-hour average, rolling by 1 hour

12

1-Year sum

13

Std1dev, 3 exceptions in hour

14

Std1dev, no exceptions

15

Std2dev, no exceptions

16

4-hour average, block

17

12-hour average, block

18

24-hour average, rolling by 1 hour

19

6-minute average, block

20

1-day sum

21

12-month sum, rolling by 1 month

22

12-month average, rolling by 1 month

23

3-hour average, block

24

7-day average, rolling by 1 day

25

1-day average, block, geometric

26

30-Operating-Day operating hour average, by 1 day

27

1-month average, block



	And/Or Standard (for or'd Standards)
	Displays the And/Or Standard for or'd standards.  Acceptable values are:

· And (A) - The data availability standard applies in addition to any other data availability standards, or is the only data availability standard.

· Or (O) - The data availability standard is one of a number of alternatives

	Emission Standard for or'd Standard
	If the Emission Standard is one of a number of alternatives, displays the Emission Standard for Or'd Standard. Examples of possible values are:

Value

Description

0

No ESIDC (Use for DA Std Only)

1

1-Minute average, 3 exceptions in hour

2

1-Minute average, block

3

1-day average, block

4

Daily averages, 2 exceptions in 30-day

5

30-day average, rolling by 1 day

6

1-hour average, block

7

4-day average, rolling by 1 day

8

3-hour average, rolling by 1 hour

9

4-hour average, rolling by 1 hour

10

8-hour average, rolling by 1 hour

11

12-hour average, rolling by 1 hour

12

1-Year sum

13

Std1dev, 3 exceptions in hour

14

Std1dev, no exceptions

15

Std2dev, no exceptions

16

4-hour average, block

17

12-hour average, block

18

24-hour average, rolling by 1 hour

19

6-minute average, block

20

1-day sum

21

12-month sum, rolling by 1 month

22

12-month average, rolling by 1 month

23

3-hour average, block

24

7-day average, rolling by 1 day

25

1-day average, block, geometric

26

30-Operating-Day operating hour average, by 1 day

27

1-month average, block



	Data Availability Standard for Or'd Standard
	If the Data Availability Standard is one of a number of alternatives, displays the Data Availability Standard for Or'd Standard. Examples of possible values are:

Value

Description

1

90% hours in month

2

95% hours in quarter

3

90% averages in month

4

75% averages in month

5

85% averages in quarter

6

100% hours in quarter

7

95% hours in day

8

50% hours in 30-day

9

23 days in 30-day

10

100% hours in day




CEMS

This section displays the CEMSs associated with the emission result, as shown in the following table.

	Column
	Description

	ID
	Displays the unique identifier of the CEMS.

	Revision #
	Displays the revision number for the CEMS.  The revision number for the CEMS in the initial monitoring plan information for the CEMS should be zero (0) with the revision number incremented whenever the monitoring plan information for the CEMS is changed.  

	CEMS Type
	Indicates whether the CEMS is the Primary CEMS, or a Backup or Standby CEMS as follows:

Primary CEMS 

Only one Primary CEMS is allowed. Data from this CEMS must be reported unless they are invalid and other Standby or Backup CEMSs exist.

Standby CEMS

You may have one to 100 Standby CEMSs.  CEMSs must be installed and undergoing all normal operation and quality assurance requirements.  Data from Standby CEMSs may be used if the data from the Primary CEMS are invalid. Data from Standby CEMSs must be used from the first Standby CEMS with valid data in number order from lowest to highest.

Backup CEMS
You may have one to 100 Backup CEMSs.  Backup CEMSs are installed only when needed.  Quality assurance checks must be conducted prior to use of data from Backup CEMSs. Data from Backup CEMSs may be used if the data from the Primary CEMS and all -- if any -- Standby CEMSs are invalid. Data from Backup CEMSs must be used from the first Backup CEMS with valid data in number order from lowest to highest.

	Status
	Displays the current status of the CEMS.

	Phase 1 Submitted
	Indicates the date on which the CEMS was submitted for Phase 1 approval.

	Phase 3 Approved
	Indicates the date on which the CEMS received Phase 3 approval.


	Button
	Description

	[image: image33.jpg]



	Clicking View next to a CEMS displays the View CEMS page, which contains detailed information about the CEMS.


 XE "View CEMS " \* MERGEFORMAT 

 XE "Units " \* MERGEFORMAT 

 XE "Type " \* MERGEFORMAT 

 XE "Status " \* MERGEFORMAT 

 XE "Revision # " \* MERGEFORMAT 

 XE "Phase 3 Approved " \* MERGEFORMAT 

 XE "Phase 1 Submitted " \* MERGEFORMAT 

 XE "Penalty Factor " \* MERGEFORMAT 

 XE "Parameter " \* MERGEFORMAT 

 XE "Opacity/Non-Opacity " \* MERGEFORMAT 

 XE "Monitoring Point Code " \* MERGEFORMAT 

 XE "ID " \* MERGEFORMAT 

 XE "Emission Result " \* MERGEFORMAT 

 XE "DEP ID " \* MERGEFORMAT 

 XE "CEMS Manual Revision # " \* MERGEFORMAT 

 XE "Basis of Measurement " \* MERGEFORMAT View CEMS

The View CEMS page displays detailed information about a CEMS for an emission result at a facility.  From this page, you can also view details about the emission result and the analyzers associated with the CEMS.  Information about the structure and options available on this page appear in the following sections.

[image: image34.jpg]Commonwealth of Pennsylvania
nt of Environmental Protection

Bureau of Air Quality

~Hoe
- Create Synchronization Fes

Correspondence

- Send Message

- View allMessages
Inbox

2008-11-27 00:00:000

From: INTUSER.

To: EXTUSER

2008-11-27 00:00:000

From: INTUSER.

To: EXTUSER

his 5 3 longersubjct

Home ~=> View Facilty Configuration ~—> View CEMS

w CEMS

PRIMARY

Enission Resul:
DEP ID:

Type:
Revision # 1
CEMS Manual Revision

Oacty % [V |
18210
PRIMARY

. s

Penaty Factor
Phase Submitedt 070412007
752007

Opacty

Phase 3 Approvert
Opactyon-Opacy:

Opacity Specifications
Tine without
Corrective
Meintenance:

180haus

Opacty Relative
Aceuracy,
1-minute averages:

Opacty Relative:
Accurscy,

averege of 15 1-minute '
averages:

Das System

Accurscy,

fomin aversges:

Das System

ccuracy, 1-our
averages:

1%

1% Opacty

1% Opacty

Analyzers

n# Parameter Units

Measurement

Basisof  Monitoring

Point Code Status

opacty %

oprcty % a

o1 Pencing Phase 2

o1 approved

P4 Dept. of Emvironmental Protection

For assistance, please call DEP at (717) 705.3768

between the hours of &:00 AM to 430 PM or send an e-

ep-efactshelpdeskteam@state. pa.us.

DEP Home | CEM Home | Contacts | Help | Logout|

mailto





Basic Information

The Basic Information section contains the following information about the CEMS:

	Field Label
	Description

	Emission Result
	Displays the emission result with which the CEMS is associated.

	DEP ID
	Displays the unique DEP identifier of the CEMS.

	Type
	Indicates whether the CEMS is the Primary CEMS, or a Backup or Standby CEMS as follows:

Primary CEMS 

Only one Primary CEMS is allowed. Data from this CEMS must be reported unless they are invalid and other Standby or Backup CEMSs exist.

Standby CEMS

You may have one to 100 Standby CEMSs.  CEMSs must be installed and undergoing all normal operation and quality assurance requirements.  Data from Standby CEMSs may be used if the data from the Primary CEMS are invalid. Data from Standby CEMSs must be used from the first Standby CEMS with valid data in number order from lowest to highest.

Backup CEMS
You may have one to 100 Backup CEMSs.  Backup CEMSs are installed only when needed.  Quality assurance checks must be conducted prior to use of data from Backup CEMSs. Data from Backup CEMSs may be used if the data from the Primary CEMS and all -- if any -- Standby CEMSs are invalid. Data from Backup CEMSs must be used from the first Backup CEMS with valid data in number order from lowest to highest.

	Revision #
	Displays the revision number for the CEMS.  The revision number for the CEMS in the initial monitoring plan information for the CEMS should be zero (0) with the revision number incremented whenever the monitoring plan information for the CEMS is changed.  

	CEMS Manual Revision #
	Displays the CEM Manual Revision Number under which the CEMS was obtained or is requesting approval.

	Penalty Factor
	Displays the penalty factor for the CEMS.

	Phase 1 Submitted
	Indicates the date on which the CEMS was submitted for Phase 1 approval.

	Phase 3 Approved
	Indicates the date on which the CEMS received Phase 3 approval.

	Opacity/Non-Opacity
	Indicates whether the CEMS is opacity or non-opacity.


	Button
	Description

	[image: image35.jpg]



	Clicking this button opens the View Emission Result page with more detailed information about the emission result.


Analyzers

This sections displays information about the analyzers associated with the CEMS, as described in the following table.

	Column
	Description

	ID
	Displays the unique identifier for the analyzer.

	Revision #
	Displays the revision number for the analyzer.  The revision number for the analyzer in the initial monitoring plan information for the analyzer should be zero (0) with the revision number incremented whenever the monitoring plan information for the analyzer is changed.  

	Parameter
	Displays the Parameter/Pollutant for the analyzer. Examples of possible values are:

CE

CO

C02

Culm Gas %

Flow

Fuel Rate

H2O

H2S

HC

HCl

HCl Reduction

Heat Input

NO

NO2

NOx

NOx Allowable

O2

Opacity

Pressure

SO2

SO2 Allowable

SO2 Reduction

Steam Flow

Temperature

TRS

VCM

VOC



	Units
	Displays the units of measurement for the analyzer. Examples of possible values are:

%

Btu/hr

cfh

Cfm

Degrees F

gph

gpm

lbs/hr

lbs/Mbtu

lbs/ton

Mbtu/hr

Mcfh

ppm

psi



	Basis of Measurement
	Displays the basis of measurement for the analyzer. Examples of possible values are:

· Wet

· Dry

· N/A

	Monitoring Point Code
	Displays the monitoring point code for the analyzer.  Examples of possible values are:

· For outlet, displays letter O followed by numeral to uniquely identify analyzer

· For inlet, displays letter I followed by numeral to uniquely identify analyzer

· For Primary Temperature, displays letter P followed by numeral to uniquely identify analyzer

· For Secondary Temperature, displays letter S followed by numeral to uniquely identify analyzer

	Status
	Displays the current status of the analyzer.


	Button
	Description

	[image: image36.jpg]



	Clicking View opens the View Analyzer page with more detailed information about the analyzer.


 XE "View Analyzer " \* MERGEFORMAT 

 XE "Units of Measurement " \* MERGEFORMAT 

 XE "Serial Number " \* MERGEFORMAT 

 XE "Sample Interface Technique " \* MERGEFORMAT 

 XE "Revision # " \* MERGEFORMAT 

 XE "Opacity/Non-Opacity " \* MERGEFORMAT 

 XE "Monitoring Point Code " \* MERGEFORMAT 

 XE "Manufacturer " \* MERGEFORMAT 

 XE "Linearity Limit in Analyzer's Unit of Measurement " \* MERGEFORMAT 

 XE "Linearity Limit as % of Reference Value " \* MERGEFORMAT 

 XE "Full Scale Value " \* MERGEFORMAT 

 XE "Equivalent Reading at Emission Standard Level " \* MERGEFORMAT 

 XE "Description " \* MERGEFORMAT 

 XE "DEP ID " \* MERGEFORMAT 

 XE "Calibration Error Limit " \* MERGEFORMAT 

 XE "Basis of Measurement " \* MERGEFORMAT 

 XE "And/Or Standard " \* MERGEFORMAT 

 XE "Analytical Technique " \* MERGEFORMAT 

 XE "% of Refer. Value " \* MERGEFORMAT 

 XE "% of Equiv. Value " \* MERGEFORMAT View Analyzer

The View Analyzer page displays detailed information about an analyzer for a CEMS. Information about the structure and options available on this page appear in the following sections.

[image: image37.jpg]. CEMDPS

" Commonwealth of Pennsylvania
Department of Environmental Protection
5 Bureau of Air Quality

Quick Links.

~Home.
- Create Synchronization Fles

Correspondence

- Send Message

- View AllMessages
Inbox

2006-11-27 00:00:000

From: INTUSER.

To: EXTUSER

2008-11-27 00:00:000

From: INTUSER.

To: EXTUSER

| s 3 onger subject

Horme ~=» View Facilty Configuration - View Analyzer

View Analyzer
Opacity %

Basic Informati
DEP ID: 6229

Revision # 3

Basie of Measurement:  NiA
Montoring Poit Code: 01

Serialumber 120812
Full Seale Value: 100%

Ectivelert Reading at

Emission Standerd Levet: %0 %

Linearity Lini a5 ™
% of Reference Vale:

Linearity Lint in Anlyzer's 3%
Ut of Measurement:

OpactyNon-Opacty.  Opacty

Analyzer Model Information
(o analyzer madel information avaiiable)

General Specification Information
Menufacturer's claimed

nearty as 1

% of reference value:

Menufacturer's ciimed

nearty as s

unit of measuremert:

Menutacturer's ciimed

7-say callbration error

o 2

% of equivalent value
o emission standarc:
Menutacturer's ciaimed
7-say calbration error
% o reference value:

2

Menutacturer's ciimed
7-say callbration error
Uit of measuremert:

2

Menufacturers clamed
cycletime in seconds:

Opacity Specifications
Expected Normal
Resding a%

Expected Maximum
Reading

Conformatian
certfcate Obtainect
Monitor Patrlength:  50.2 Feet
Enission Outiet
Pathlenth:
Deta Resorder Resolution

% of Eqivalent

Reading 1
o Emission Lini:

15%

Yes

2307 Feat

Aralyzer's unt of
measurement: 1

seconds: 1

Number of Cycles Per
Hou, Measure:
Number of Cycles Per
Hou, Recorc:

Number af Zero and
Clbration 7
Checks per Week:

360

&

Calibration Ervor Limits

Calibration

Erition  %ofEquiv.Value % of Refer. Value

Units of
Measurment

Andior Standard

2ahowr Drit__ A s

and

PA Dept.of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (T17) 7053768
between the hours of £:00 AM to 430 PM or send an e-mail to
ep-efactshelpdeskteam@state. pa.us.





Basic Information

The Basic Information sections presents the following information about the analyzer:

	Field Label
	Description

	DEP ID
	Displays the unique DEP identifier for the analyzer.

	Revision #
	Displays the revision number for the analyzer.  The revision number for the analyzer in the initial monitoring plan information for the analyzer should be zero (0) with the revision number incremented whenever the monitoring plan information for the analyzer is changed.  

	Basis of Measurement
	Displays the basis of measurement for the analyzer. Examples of possible values are:

· Wet

· Dry

· N/A

	Monitoring Point Code
	Displays the monitoring point code for the analyzer. Examples of possible values are:

· For outlet, displays letter O followed by numeral to uniquely identify analyzer

· For inlet, displays letter I followed by numeral to uniquely identify analyzer

· For Primary Temperature, displays letter P followed by numeral to uniquely identify analyzer

· For Secondary Temperature, displays letter S followed by numeral to uniquely identify analyzer

	Serial Number
	Displays the serial number for the analyzer.  If the actual analyzer has not yet been received, this field is blank.

	Full Scale Value
	Displays the full scale value for the analyzer in units of analyzer measurement.  

	Equivalent Reading at Emission Standard Level
	Displays the equivalent reading at emission level for the analyzer at the lowest applicable emission standard.  Determination of this value is explained in the Continuous Source Monitoring Manual.  

	Linearity Limit as % of Reference Value
	Displays the linearity limit as % of reference value for the analyzer.

	Linearity Limit in Analyzer's Unit of Measurement
	Displays the linearity limit in units of measurement for the analyzer. 

	Opacity/Non-Opacity
	Indicates whether the analyzer is opacity or non-opacity.


Analyzer Model Information

This section contains model information for the analyzer as follows:

	Field Label
	Description

	Manufacturer
	Displays the manufacturer name for the analyzer.

	Description
	Displays the model description of the analyzer.

	Analytical Technique
	Displays the analytical technique for the analyzer. Examples of possible values are:

2nd Derivative UV

Chemiluminescence

Coulometric Titration

Differential Pressure

Diffusion/absorption

Double Pass Transmissometry

Electrochemical Cell

Fluorescence 

Fuel Cell

Fuel Sampling

GC 

Ion Mobility Spectrometry

IRGFC 

Lead Acetate Tape

NA

NDIR 

NDUV 

Orifice Plate

Paramagnetic 

Single Pass Transmissometry

Thermal Mass Flow

Thermocouple 

Ultrasonic 

UV Diode Array

Vortex Flowmeter

Wheel Meter



	Sample Interface Technique
	Displays the sample interface technique for the analyzer. Examples of possible values are:

· Extractive

· Dilution Extractive

· In-situ

· Dilution In-situ

· Not Applicable


General Specification Information

The General Specification Information section provides an overall description of the analyzer.

Calibration Error Limits

This section describes the calibration error limits for the analyzer, as shown in the following table.

	Column
	Description

	Calibration Error Limit
	Displays the calibration error limit for the analyzer. 

	% of Equiv. Value
	Displays the Calibration Error Limit Value  - % of Equiv. Value (as specified in the Continuous Source Monitoring Manual).  

	% of Refer. Value
	Displays the Calibration Error Limit Value - % of Refer. Value (as specified in the Continuous Source Monitoring Manual).

	Units of Measurement
	Displays the Calibration Error Limit Value - Units of Measurement (as specified in the Continuous Source Monitoring Manual).  

	And/Or Standard 
	Displays And, since currently all calibration error standards are "And'd".


Monitoring Plans

 XE "Validate Submittal " \* MERGEFORMAT 

 XE "Submitted By " \* MERGEFORMAT 

 XE "Status " \* MERGEFORMAT 

 XE "Source Combination " \* MERGEFORMAT 

 XE "Primary Facility Id " \* MERGEFORMAT 

 XE "Facility Name " \* MERGEFORMAT 

 XE "Emission Result " \* MERGEFORMAT 

 XE "Company Name " \* MERGEFORMAT 

 XE "CEMS " \* MERGEFORMAT 

 XE "Analyzers " \* MERGEFORMAT Monitoring Plan Page

The Monitoring Plan page displays basic information about your facility's monitoring plan and its source combinations, emission results, CEMSs, and analyzers. You can also add and make changes to source combinations, emission results, CEMSs, and analyzers from this page. Descriptions of the Monitoring Plan page's structure and options appear below. 

[image: image38.jpg]c h of P =
EMDPS Bosrnant of nvironmsdtal Proton ;
Bureau of Air Quality

Home -~ Ect Montoring Plan
Monitoring Plan #182
[ comespondence

“Send essage Basic Information

- View AllVessages Prinary Facity i 510331

Inbox Company Name: CASTLE RUBBERLLC

| 2008-11-27 0000000 Facity Name: CASTLE RUBBER LLCEAST BUTLER BORO
 From: NTUSER

Status: Revision
To: EXTUSER

s Subnitted By. ot specitied A3
| 2008-11-27 0000000 Remave Montoring Plan

From: INTUSER.

o EXTUSER View all llotes for this Montor

Record Koeping Information Evi. 543 [VEaT Eatosrars | [emave
A tnformation suw. s42 [V EdTore

E9 Configuration Information Expand &1 Colapze All
Glick the B button to expand

19 Plan

his 5 3 ongersubject

A Dept. of Enviranmantal Protection DEP Home | CEM Home | Contacts | Help | Logout]

For assistance, please call DEP at (717) 7053768
between the hours of £:00 AM to 430 PM or send an e-mail to
ep-efactshelpdeskteam@state. pa.us.





Basic Information

The Basic Information section displays four pieces of information associated with the monitoring plan as follows:

	Field Label
	Description

	Primary Facility Id
	Displays the facility ID for which the monitoring plan is being submitted.

	Company Name
	Displays the name of the company associated with the monitoring plan.

	Facility Name
	Displays the name of the facility associated with the monitoring plan.

	Status
	Displays the status of the monitoring plan as follows:

Status

Description

Initiated

A monitoring plan is considered Initiated if you have begun entering data for your monitoring plan but have not yet submitted the information for DEP review.  Only facility users may work with the submittal package while it has this status.

Submitted

A monitoring plan is considered Submitted if you have submitted your monitoring plan information for DEP review.  Only DEP reviewers and approvers may work with the submitted data when the monitoring plan has this status.  You will be able to view the information, but not change it.

Submitted (Partial Submittal)

This status is similar to the Submitted status, but is used to identify a partial submittal.  Partial Submittals normally occur with quarterly reports.  

Review

Once you submit your monitoring plan, the status changes to Review as DEP reviewers examine your submittal.

Revision

If DEP reviewers find issues with a submittal, they may reject it and request that data be changed or verified by the facility.  In this instance, the monitoring plan is given the status of Revision, and you may revise the information and resubmit the plan.  Only facility users may work with the monitoring plan information while it has this status.

Review Complete

After reviewers evaluate and render a decision on the monitoring plan submission, they move the monitoring plan into Review Complete status.  At this point, the submission is waiting for a DEP approver to login and verify the reviewer's decision.  No one can change the monitoring plan submission through the CEMDPS application while it has this status. Approvers automatically receive an email notification indicating that a reviewed submission is awaiting their approval.

Approved

This is the final status of a submission.  This status indicates that an approver approved the decision made by a reviewer.  When the submission enters Approved status, you, and other defined users at your facility, automatically receive an email notification from the CEMDPS. No one may change the monitoring plan data through the CEMDPS once it reaches this status.  Facility users and DEP approvers and reviewers may still view the monitoring plan information through the PDF file.

Hold

A reviewer or approver may place the monitoring plan submission in Hold status.  The Hold status remains until the submission is reassigned.



	Submitted By
	Displays the name of the person who submitted the monitoring plan. The Edit button allows you to edit the submitter information.  See the Create/Edit Submitter Information page for details..


The Remove Monitoring Plan Link

The Remove Monitoring Plan link lets you delete the monitoring plan.  Clicking this link opens the Delete <Item> page, which allows you to confirm or cancel the deletion.

The View all Notes for this Monitoring Plan Link

The View all Notes for this Monitoring Plan Link opens the View Notes page and allows you to view all notes associated with the components of the monitoring plan.  

Note:  The View all Notes for this Monitoring Plan link is available only in the online CEMDPS application.

Navigating the Monitoring Plan Page

The Monitoring Plan page contains three sections, Record-Keeping Information, QA Information, and Configuration Information.  Descriptions of the information and options available under each of the main sections (Record-Keeping Information, QA Information, and Configuration Information) follow in the sections below.

Record-Keeping Information

The Record-Keeping Information section displays two buttons that allow you to view, edit, or remove record-keeping (EDR 841) information about the monitoring plan.

[image: image39.jpg]ng Information EDR 841 [ View/ Edit Details |

Record-Keep




· To view or change record-keeping information (EDR 841), click the View/Edit Details button to go to the Record Keeping Information page.

· To remove all record-keeping information (EDR 841), click the Remove button. (The Remove button only displays when record-keeping information already exists for monitoring plan.)

Note:  The only time you may change information in the monitoring plan is when the status (indicated in the Basic Information section at the top of the page) is Initiated or Revised.  At all other times, you may only view monitoring plan information.

QA Information

The QA Information section displays two buttons that allow you to view, edit, or remove QA (EDR 842) information about the monitoring plan. 

[image: image40.jpg]



· To change QA information (EDR 842), click the View/Edit Details button to go to the Monitoring Plan QA Information page.

· To remove all QA information (EDR 842), click the Remove button. (The Remove button only displays when QA information already exists for monitoring plan.)

Note:  The only time you may change information in the monitoring plan is when the status (indicated in the Basic Information section at the top of the page) is Initiated or Revised.  At all other times, you may only view monitoring plan information.

Configuration Information

The Configuration Information section is organized in a hierarchy that shows source combinations associated with the monitoring plan, emission results associated with source combinations, CEMSs associated with emission results, and analyzers associated with CEMSs. Using the expand (+) and collapse (-) symbols, you can display or hide the hierarchical information.

· Click the plus sign (+) in front of any heading to view more detailed information about that section or to access more options.  Information and available options display indented beneath the heading expanded.

· Click the minus sign (-) in front of any heading to collapse (hide) the details displayed beneath it.

· Click the Expand All link to display all information and options beneath all headings at once.

· Click the Collapse All link to collapse the entire hierarchy of information, hiding all details except for the three main headings.

The following table describes the information and options available at each level of the hierarchy in the Configuration Information section.

	Hierarchy Level
	Description

	Source Combinations
	When you expand (+) the Configuration Information heading, a list of source combinations and their related summary information and options display.  

[image: image41.jpg]B Configuration Information Expand Al Collapse A1

Source Combinations (1) A4 ang s12

Basic Information EDR 812

Crenge e Addition f tlew Record
s for it

oo [rp—
Crmenus 020007

i ggprove

Number: 4599940

R Copacky 2000 Wbt

oty YO0 s of Manutacurer

£ General Information
Glick the B button to expand
£ Emission Results (1) EDR 820
Glick the B buttan to expand

EbR 043




Each source combination name and ID displays highlighted in purple with a Basic Information section summarizing the combination.  You have the option to expand (+) the General Information section, which displays general source combination information based on EDR 843, for more details. For more information, see Edit General Monitoring Plan Information (EDR 843).  The Emission Results section shows in parentheses the number of emission results associated with that source combination.  You can also expand (+) the Emission Results section to see the emission results defined for the source combination.  

Click Add to create a new source combination or click Remove to remove a source combination from the monitoring plan.  To change Basic Information or General Information, click Edit next to the appropriate section heading.  Where applicable, EDRs are indicated for your reference.

	Emission Results
	When you expand (+) the Emission Results heading under a source combination, a list of emission results for that combination displays.

[image: image42.jpg] Emission Resuits (1) A% Jzog s20

[Opacity % (DEP 1d: 10153) [Remo-

Basic Information [ E%_Jzne s20

Changs Type: Addition of llew Record

Reason for nformation

e Intial Submittal

Effective Dete: o2z82007
Basi of easurement. 1WA
Conected To "

Dats Substtution

Recirect L
Reasons b 021
Reason for Installation Regulatory Citation
PLAN Approval Cafion 1
Emission Standards| bR 022
Emission Standard Config Start Date End Date.
1-our average, biock 2rez007
Data Availability Standard bR 023
Data Availabilty Standard Config Start Date End Date.
90% averages in morth 2rez007,

EICEMS (1) DR 824
Click the B button to expand





Each emission result name and ID displays highlighted in purple with Basic Information, Reasons, Emission Standards, and Data Availability Standards sections summarizing the emission result.  The CEMS section shows in parentheses the number of CEMS associated with that emission result.  You can also expand (+) the CEMS section to see the CEMS defined for the emission result.  

Tip:  As you expand sections to move deeper into the hierarchy, the purple highlighting for each entity name becomes lighter.  For example, the source combination names are the darkest purple, emission results names are slightly lighter purple, etc.  These color variations are intended to help you remember where you are as you navigate the hierarchy.
Click Add to create a new emission result or click Remove to remove an emission result from the source combination.  To change Basic Information, Reasons, Emission Standards, or Data Availability Standards, click Edit next to the appropriate section heading.  Where applicable, EDRs are indicated for your reference.

	CEMS
	When you expand (+) the CEMS heading under an emission result, a list of CEMS for that emission result displays.

[image: image43.jpg]S cems ) A9 anm o2a

[Primary ep 1d: 10154 [Remove ]

050 Jog 02a

Changs Type: Addition of llew Record

Basic Informati

Reason fo nformation oo

Change:
Effective Date: 02282007
Type: PRIMARY
CEM Manual Revision

b s

OpactyNon-Opacty.  Opacity

B CEMS Opacity Specification Information
Glick the 3 button to expand

EbR 034

& Non-Opacity Specification Information £0r 835
Glick the 5 button to expand
i Analyzers (1) EDR 826 EDR 825
Glick the 3 button to expand




Each primary, backup, and standby CEMS name and ID displays highlighted in purple with Basic Information, CEMS Opacity Specification Information, Non-Opacity Specification Information, and Analyzers sections summarizing the CEMS.  The Analyzers section shows in parentheses the number of analyzers associated with that CEMS.  You can also expand (+) the Analyzers section to see the analyzers defined for the CEMS.  

Tip:  As you expand sections to move deeper into the hierarchy, the purple highlighting for each entity name becomes lighter.  For example, the source combination names are the darkest purple, emission results names are slightly lighter purple, etc.  These color variations are intended to help you remember where you are as you navigate the hierarchy.
Click Add to create a new CEMS or click Remove to remove a CEMS from the emission result.  To change Basic Information, CEMS Opacity Specification Information, or Non-Opacity Specification Information, click Edit next to the appropriate section heading.  Where applicable, EDRs are indicated for your reference.

	Analyzers
	When you expand (+) the Analyzers heading under a CEMS, a list of analyzers for that CEMS displays.

[image: image44.jpg]B anatyzers (1) A% Jgom s20 mm 029

[racty v 06w 1010155 [Femene |

H Basic Informati
Glick the B utton to expand

n

DR 020 KIR 825

& Analyzer Opacity and Non-Opacity Information
Gliok the  button to expand

E Analyzer Opacity Information

Glick the B utton to expand

EbR 840

Ebm 037

& Analyzer Non-Opacity Information £0% s36
(ot appicabie or apacity Anahyzers)

Calibration Error Limits _E7" |z s30

Calibration Limit ID Andior Flag

24-hour Drft B





Each analyzer name and ID displays highlighted in purple with Basic Information, Analyzer Opacity and Non-Opacity Information, Analyzer Opacity Information, Analyzer Non-Opacity Information, and Calibration Error Limits sections summarizing the CEMS.  You can expand (+) each of these sections for further information.

Tip:  As you expand sections to move deeper into the hierarchy, the purple highlighting for each entity name becomes lighter.  For example, the source combination names are the darkest purple, emission results names are slightly lighter purple, etc.  These color variations are intended to help you remember where you are as you navigate the hierarchy.
Click Add to create a new Analyzer or click Remove to remove an analyzer from the CEMS.  To change Basic Information, Analyzer Opacity and Non-Opacity Information, Analyzer Opacity Information, Analyzer Non-Opacity Information, or Calibration Error Limits, click Edit next to the appropriate section heading.  Where applicable, EDRs are indicated for your reference.


The Validate Submittal Button

The DEP requires monitoring plan data fields to be submitted in specific formats, which are indicated where applicable in the CEMDPS pages, and to follow business rules outlined in the current Continuous Source Monitoring Manual (CSMM).  At the top of the Monitoring Plan page, click Validate Submittal to have the CEMDPS check the data you entered to ensure it's in the proper format and follows CSMM business rules before you submit the plan.  After the validation process, the Monitoring Plan Submittal page displays. This page either confirms that all data was validated or lists errors that must be addressed before submitting the monitoring plan.  Please see Monitoring Plan Submittal Page for more information.

 XE "View Submittal " \* MERGEFORMAT 

 XE "Generate EDR " \* MERGEFORMAT Monitoring Plan Submittal Page

The Monitoring Plan Submittal page displays when you click the Validate Submittal button in the Monitoring Plan page to validate data before submitting your plan.  Depending on the validity of the data you entered, the Monitoring Plan Submittal page displays two types of information as follows:

· Successful Validation:  If all monitoring plan data is entered correctly, the Monitoring Plan Submittal page displays a confirmation that all monitoring plan information is valid for submission.

· List of Errors:  If there is data that fails to meet formatting or business rules for a monitoring plan submittal, the Monitoring Plan Submittal page displays a list of the errors for you to correct before submitting the monitoring plan.  The submittal page indicates the nature of the error (missing data, invalid value, etc.), the element of the plan containing the error (CEMS, Analyzer, etc.), and if applicable, the field containing invalid data.

Successful Validation

If all data in your monitoring plan is entered correctly, the Monitoring Plan Submittal page displays a confirmation that all monitoring plan information is valid for submission.

[image: image45.jpg]C‘ommnwweanhﬁmm‘ylvlnl-
partment of Environmental Protection P

~ Bureau of Air Quality

Quick Links.

- Send Message
- View AllMessages

| 2008-11-27 0000000
| From WTUSER

To: EXTUSER
|2008-11-27 0000000
From nTusER

To: EXTUSER

his 5 3 ongersubject

Home ~~> it Manitoring Plan ~-> Subm Montoring Plan

Monito

g Plan Submittal

The Monitoring Flan has been validated successfuly.

[ submitar | [ swmitts oer ][ Generste EoR

P Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (T17) 7053768
between the hours of £:00 AM to 430 PM or send an e-mailto
ep-efactshelpdeskteam@state.pa.us.





Note:  A confirmation that all monitoring plan data has been validated successfully does not indicate that the monitoring plan has been submitted to the DEP.  It just confirms that all required data is entered, that the data entered is formatted correctly, and that the data follows appropriate business rules in preparation for submittal.

The View Submittal Button

If your monitoring plan information is validated, the View Submittal button displays.  Clicking this button allows you to view or save a document in PDF format that contains all monitoring plan information to be submitted to the DEP.  

Note:  You must have Adobe® Acrobat in order to view the PDF document generated from the View Submittal button.

The Submit to DEP Button

If your monitoring plan information is validated, the Submit to DEP button displays.  Clicking this button submits your monitoring plan to the DEP for review. When your monitoring plan is submitted, the Monitoring Plan Submittal page displays a message confirming that your monitoring plan was submitted.  The Back to Home Page button returns you to the facility home page.

Note:  The Submit to DEP button displays only for users working in the online CEMDPS.  Users working in the disconnected client application must click Generate EDR to create an EDR text file and upload it from the Facility Home Page in the online CEMDPS application.

The Generate EDR Button

If your monitoring plan information is validated, the Generate EDR button displays.  Clicking this button allows you to view or save a text file containing all EDR information for the monitoring plan submittal.

Note:  Users working in the disconnected client application should use the Generate EDR to create an EDR text file, then upload the EDR file into the online CEMDPS from the Facility Home Page in the online application.

List of Errors

If there is data that fails to meet formatting or business rules for a monitoring plan submittal, the Monitoring Plan Submittal page displays a list of the errors for you to correct before submitting the monitoring plan.  The submittal page indicates the nature of the error (missing data, invalid value, etc.), the element of the plan containing the error (CEMS, Analyzer, etc.), and if applicable, the field containing invalid data.

[image: image46.jpg]CEMDPS

Commonwealth of Pennsylvania

;;M ent of Environmental Protection
‘ Bureau of Air Quality

| Home

|- Ceste Syrevonzaon s

Correspondence

- Send Message

- View AllMessages
Inbox

2008-11-27 00:00:000

From: INTUSER

To: EXTUSER

2008-11-27 00:00:000

From: INTUSER.

To: EXTUSER

his 5 3 ongersubject

Home ~~> it Manitoring Plan ~-> Subm Montoring Plan

Monitoring Plan Submittal

The Moritoring Flan has errors.
@ Informetion: Fie Atiachment with G Plan s Nul - Enter 2 vl value

Genersl nformatian for Source Cambination 752.:File Attachment wih Equipment Names s Null - Enter 2 val value
‘General nformation for Source Combination 752  File Atiachment wih Equipment Parameters is Nul - rter a vald vabie
(Genersl nformatian for Source Cambination 752. File Atiachment with Flow Diagrams is Nul - Enter a vald value:
Enission Stanard information s missing for Emission Resuk# 1956

CEMS Non-Opacy Information is missing for Opachy CEVS #2283

‘Opacy Information has been erterect for Non-Opacty CEMS # 2283, Remove invald information

Analyzer 6207 - Analyzer Opacityion-Opacty Corer is Nul - Erter a val vakie:

‘Anelyzer Callration Error Link Information is missing for Analyzer # 6207

Haring Plan

P4 Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (717) 7053768
between the hours of £:00 AM to 430 PM or send an e-mailto
ep-efactshelpdeskteam@state. pa.us.





The Edit Monitoring Plan Button

If the Monitoring Plan Submittal page lists errors with your monitoring plan data, the Edit Monitoring Plan button appears at the bottom of the page.  Clicking this button returns you to the Monitoring Plan page, allowing you to correct the errors and validate the submittal again.

 XE "Note Text " \* MERGEFORMAT Add Note Page

The Add Note page allows you to include a note along with the other information entered about a component of a monitoring plan, test protocol, or certification/test report.  For example, you might add an explanatory note about an emission result in your monitoring plan.  DEP reviewers and approvers can view these notes along with your submittals.

Note:  This page is available only in the online CEMDPS application.  Users in the disconnected CEMDPS application do not have access to this page.

To add a note, follow the instructions for each field, as listed below.

[image: image47.jpg]- Send Message
- View AllMessages

2008-11-27 00:00:000
 From: NTUSER
To: EXTUSER

|205-1127 000000
From: INTUSER.
To: EXTUSER

his 5 3 ongersubject

Commonwealth of Pennsylvania
ent of Environmental Protection
Bureau of Air Quality
Add Note
Record Keeping Information for Monitoring Plan #307

Return to form

Nete Text:

P Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (T17) 7053768
between the hours of £:00 AM to 430 PM or send an e-mailto
ep-efactshelpdeskteam@state.pa.





	Field Label/Link
	Activity

	Return to form
	Clicking this link takes you back to the page from which you clicked the Add Note link.

	Note Text
	Enter note text in the text box provided.


	Button
	Description

	Save
	Clicking Save saves the information and displays the note text in the View Notes page.

	Cancel
	Clicking Cancel takes you to the View Notes  page without saving changes.  If there are other notes created for the item, those notes appear in the View Notes page.  If there are no other notes, the View Notes page displays the text No notes entered.


 XE "Note " \* MERGEFORMAT 

 XE "Date " \* MERGEFORMAT 

 XE "Added by " \* MERGEFORMAT View Notes Page

The View Notes page displays all notes associated with a component of a monitoring plan, test protocol, or certification/test report.  You can view notes for one component, such as an emission result in a monitoring plan, or all notes for an entire submittal.  (See Monitoring Plan Page, Test Protocol Page, and Certification/Test Report Page for information about viewing notes for entire submittals.) DEP reviewers and approvers can view notes along with your submittals.

Note:  This page is available only in the online CEMDPS application.  Users in the disconnected CEMDPS application do not have access to this page.

The table below describes the information displayed in the View Notes page and the options available. 

[image: image48.jpg]Commonwealth of Pennsylvania
ent of Environmental Protection
Bureau of Air Quality

- Send Message
- View AllMessages

(—

| 2005-11-27 000000
 From: NTUSER
o xTusER

| this s 2 fonger subject

View Notes

Record Keeping Information for Monitoring Plan #307

Return o form

[Added by: EXT USER.

[Added by: EXT USER
Date: 077312007
lote: Etered 511612007

P Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (T17) 7053768
between the hours of £:00 AM to 430 PM or send an e-mailto

ep-efacts!

helpdeskteam@state.pa.





	Field Label
	Activity

	Return to form
	Clicking this link takes you back to the page containing the component or submittal for which you viewed notes.

	Added by
	Displays the name of the user who added the note.

	Date
	Displays the date on which the note was entered.

	Note 
	Displays the note text.


Record Keeping Information

 XE "Results from tests, audits, and recalibrations reported on calendar...? " \* MERGEFORMAT 

 XE "Reports to be submitted in format specified in CEM Manual and signed...? " \* MERGEFORMAT 

 XE "Reports specified in CEM Manual to be reported on calendar quarter basis? " \* MERGEFORMAT 

 XE "Report to be submitted by 30th day after quarter close? " \* MERGEFORMAT 

 XE "Record of repairs, adjustments, or maintenance? " \* MERGEFORMAT 

 XE "Record of corrective actions in response to exceedances or invalid data? " \* MERGEFORMAT 

 XE "Reason for Information Change " \* MERGEFORMAT 

 XE "Process and control equipment data that affect emissions? " \* MERGEFORMAT 

 XE "Monitoring data available via telemetry in accordance with...? " \* MERGEFORMAT 

 XE "Effective Date " \* MERGEFORMAT 

 XE "EDR 841 " \* MERGEFORMAT 

 XE "Edit Record Keeping Information " \* MERGEFORMAT 

 XE "Data necessary for conversion to units of standard? " \* MERGEFORMAT 

 XE "Data and results for all tests, audits, and recalibrations? " \* MERGEFORMAT 

 XE "Copies of Phase I application, Phase II protocol, Phase III report...? " \* MERGEFORMAT 

 XE "Comments " \* MERGEFORMAT 

 XE "Cause, time periods, and magnitude of emissions which exceed...? " \* MERGEFORMAT 

 XE "Cause and time periods for invalid data? " \* MERGEFORMAT 

 XE "All monitoring system results reduced to 1-hr avgs in terms of...? " \* MERGEFORMAT 

 XE "All monitoring system results for Opacity and Temperature reduced to...? " \* MERGEFORMAT 

 XE "All measurements on at least the minimum cycle time? " \* MERGEFORMAT 

 XE "All 1-hr and 1-min avgs, as applicable? " \* MERGEFORMAT Edit Record Keeping Information (EDR 841)
The Edit Record Keeping Information page contains record keeping information about your monitoring plan.  You must enter record keeping information with the monitoring plan for each facility. 

To add or edit Record Keeping Information, follow the instructions for each field, as listed below.  
[image: image49.jpg]Commonwealth of Pennsylvania

Bureau of Air Quality

CEMDPS D ent of Environmental Protection P
L.

Quick Links

| ~ome
|- Creste Syrchvonization s _|

Correspondence

~Send Message

-View Al Messages
Inbox

2006-11-27 0000000

From: NTUSER

To: EXTUSER

2006-11-27 0000000

From: NTUSER

To: EXTUSER

Home ~=> Edit Maritaring Plan ~~>Edit Recard Keeping Informatian

Edit Record Keeping Informat

EDR 041

View Hotes | Ad Note

| s 3longer subject

R [ (s s mmtasny)

Allmonioring system resuts recucert o 1-r
g interms of standard per Gualty Ves <
Assurance Secton of CEM Manual?

Allmonioring system resuts for Opacty and
Tempersture reducedta 1-minute avgs per [Ves =
@ Section of CEM Manual?

Does chronological il containthe following
for s years:
Allmeasurements an
. atleastthe minimun [Yes <
cycletine?

All1-hr and 1-in
avgs, as applicable?

Cause, time periods,
and magniucte of
enissions which
excesd standards?

Dt andl resuls for
x altests, audts and  [Ves <
resallrations?

Record of repairs,
- adustmerts, or Yes <
meintenance?

Deta necessary for

. conversionto units of [Ves =

standard?

Couse andtine
. perious fornvalid [Ves <
data?
Process and cortral

. ecqipment detathat  [Ves <
affect emissions?

Copies of Phass |
applicaton, Phase I

. protocol Phasell [Ves <
report and related
correspondence?
Recard of carrective
actions i response

' toexceedancesor 1% -

invalid data?
Reports specifiec in CEM Manual o be. T =
reported on calendar cuarter basis?
Resuls from tests, aucts s recalbrtions [7— =
reported on calendar cuater basis?
Report o be submited by 30th day after

Yes =

auarter close?
Reparts to be submited i format specifiec
in CEM banual an signed by responsible  [Ves <

person?
Monitoring data avaiable via telemetry in

aceordance wih CEM Manual? (not recuired [Ves =
for allCEMSs):
[Corments RE B

Tnitial Swmmiceal =
I |

Commerts:

Reason for Information Change:

[save]

P4 Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (T17) 7053768
between the hours of £:00 AM to 430 PM or send an e-mail to
ep-efactshelpdeskteam@state. pa.us.





	Field Label/Link
	Activity

	View Notes
	Clicking the View Notes link opens the View Notes page, which allows you to view all notes associated with this record keeping information.

Note:  This link is active only in the online CEMDPS application.  

	Add Note
	Clicking the Add Note link opens the Add Note page, which allows you to enter a note for this recording keeping information.

Note:  This link is active only in the online CEMDPS application.  

	Effective Date
	Enter the effective date of the submitted information in the format mm/dd/yyyy or click the calendar icon to select a date from a calendar.  (See Date Selection for information on using the calendar to choose a date.)

	All monitoring system results reduced to 1-hr avgs in terms of standard per Quality Assurance Section of CEM Manual? 
	From the drop-down list, choose Yes, No, or Not Applicable.


	All monitoring system results for Opacity and Temperature reduced to 1-minute avgs per QA Section of CEM Manual? 
	From the drop-down list, choose Yes, No, or Not Applicable.


	Does chronological file contain the following for 5 years?
	

	-All measurements on at least the minimum cycle time?
	From the drop-down list, choose Yes, No, or Not Applicable.


	-All 1-hr and 1-min avgs, as applicable?
	From the drop-down list, choose Yes, No, or Not Applicable.

	-Cause, time periods, and magnitude of emissions which exceed standards? 
	From the drop-down list, choose Yes, No, or Not Applicable.

	-Data and results for all tests, audits and recalibrations?
	From the drop-down list, choose Yes, No, or Not Applicable.

	-Record of repairs, adjustments, or maintenance? 
	From the drop-down list, choose Yes, No, or Not Applicable.

	-Data necessary for conversion to units of standard?
	From the drop-down list, choose Yes, No, or Not Applicable.

	-Cause and time periods for invalid data? 
	From the drop-down list, choose Yes, No, or Not Applicable.

	-Process and control equipment data that affect emissions?
	From the drop-down list, choose Yes, No, or Not Applicable.

	-Copies of Phase I application, Phase II protocol, Phase III report and related correspondence?
	From the drop-down list, choose Yes, No, or Not Applicable.

	-Record of corrective actions in response to exceedances or invalid data?
	From the drop-down list, choose Yes, No, or Not Applicable.

	Reports specified in CEM Manual to be reported on calendar quarter basis? 
	From the drop-down list, choose Yes, No, or Not Applicable.

	Results from tests, audits and recalibrations reported on calendar quarter basis?
	From the drop-down list, choose Yes, No, or Not Applicable.


	Report to be submitted by 30th day after quarter close?
	From the drop-down list, choose Yes, No, or Not Applicable.


	Reports to be submitted in format specified in CEM Manual and signed by responsible person?
	From the drop-down list, choose Yes, No, or Not Applicable.

	Monitoring data available via telemetry in accordance with CEM Manual? (not required for all CEMSs): 
	From the drop-down list, choose Yes, No, or Not Applicable.

	Comments
	Enter up to 160 characters of comments, as necessary.  

	Reason for Information Change
	Enter a reason for the information change up to 50 characters.


	Button
	Description

	Save
	Clicking Save saves the information and returns you to the Monitoring Plan page.

	Cancel
	Clicking Cancel returns you to the Monitoring Plan page without saving changes.


QA Information

 XE "Zero gases in accordance with QA Section of CEMM? " \* MERGEFORMAT 

 XE "Thermocouples calibrated using NIST/ASTM procedures...? " \* MERGEFORMAT 

 XE "Reference material/signal to be applied as close to sample acquisition...? " \* MERGEFORMAT 

 XE "Records of manual adjustments maintained? " \* MERGEFORMAT 

 XE "Record of changes to "K-factors" or other constants maintained? " \* MERGEFORMAT 

 XE "Reason for Information Change " \* MERGEFORMAT 

 XE "Quarterly mid check to be conducted at 40%-60% of range near...? " \* MERGEFORMAT 

 XE "Quarterly low check to be conducted at 0%-30% of range or lower...? " \* MERGEFORMAT 

 XE "Quarterly linearity to be conducted on all measurement device ranges? " \* MERGEFORMAT 

 XE "Quarterly high check to be conducted at 80%-100% of range, or higher...? " \* MERGEFORMAT 

 XE "QA per 40 CFR 75, Appendix D, 2.1.6, & all subparagraphs...? " \* MERGEFORMAT 

 XE "Published F-factors used? " \* MERGEFORMAT 

 XE "PDF file containing QA Plan " \* MERGEFORMAT 

 XE "Multicomponent gases free from interferents and non-reactive? " \* MERGEFORMAT 

 XE "Measurement devices to be adjusted if cal error performance...? " \* MERGEFORMAT 

 XE "Linearity test to be conducted if post-maintenance checks...? " \* MERGEFORMAT 

 XE "Fuel Sampling/analysis to determine F-factors? " \* MERGEFORMAT 

 XE "F-factors for non-uniform fuels determined per QA Section of CEMM? " \* MERGEFORMAT 

 XE "Effective Date " \* MERGEFORMAT 

 XE "EDR 842 " \* MERGEFORMAT 

 XE "Edit Monitoring Plan QA Information " \* MERGEFORMAT 

 XE "Data validation to comply with QA Section of CEMM? " \* MERGEFORMAT 

 XE "Data reduction to comply with QA Section of CEMM? " \* MERGEFORMAT 

 XE "Daily zero check to be conducted at 0%-30% of range...? " \* MERGEFORMAT 

 XE "Daily zero and cal to be conducted on all measurement device ranges? " \* MERGEFORMAT 

 XE "Daily cal check to be conducted at 40%-100% of range...? " \* MERGEFORMAT 

 XE "Comments " \* MERGEFORMAT 

 XE "Calibration gases prepared per EPA Traceability Protocol? " \* MERGEFORMAT 

 XE "Calibration gases for monitors with critical orifices approximate sonic...? " \* MERGEFORMAT 

 XE "Cal error checks to be conducted prior to maintenance if possible? " \* MERGEFORMAT 

 XE "Cal error checks to be conducted following maintenance? " \* MERGEFORMAT 

 XE "Annual relative accuracy test audit to be conducted on all monitoring...? " \* MERGEFORMAT Edit Monitoring Plan QA Information (EDR 842)
The Create/Edit Monitoring Plan QA Information page records quality assurance information as part of the monitoring plan.  You must enter QA information with the monitoring plan for each facility.
To add or edit Monitoring Plan QA Information, follow the instructions for each field, as listed below.  
Note:  Due to the large number of data fields available on this page, three pictures are used below to display all fields.
[image: image50.jpg]CEMDPS ‘Nmﬁ:&rm:;;m

Bureau of Air Quality

{— \
| From: INTUSER

|205-1127 0000000
From mTUsER
o ExtuseR

I

Home ~> it Manitaring Plan ~-> Edt Manitoring Plan G Information

Edit Monitoring Plan QA Information

DR 042

View Notes | Ad Note

Effective Date: fo17302007 | st v maniaayyyy)

Deta validstion to
comply with

@ Section of CEM
Manual (CEMM)?
PDF fle containing
Q4 Plan

Deta recucton o

comply with s <
Qi Section of CEMM?

Yes B

Biowse. |  EDRAD good fultxt

Cal error checks to
e conducted

prior to maintenance.
if possible?

ol Error shecks to
e conductedt
folowing
maintenance?

Yes =

Yeos =

Linearty Test to be:
condcted f post-
maintenance

checks exceed twice
performance
specification?

Daly zero an calto
e conducted

on all measurement.
device ranges?

Reference
materiaisignalto be
applied

as claseto sample
acquistion poirt a5
possile?
Measuremert devices
to be adusted

ifcal ertor
performance
specifications

Yes =

Yeos =





[image: image51.jpg]Daily zero checkto
e conducted ot 0%-
E

of range or lower
than lowest reaing
expected?

Daily cal check to be:
condcted st 40%-
100%

of range or near
norml reacing
expecte?
Quartely nearty to
e conducted on
allmeasurement
device ranges?
Quartely low check
to'he condlcted
0%-30%

of range or lower
than lowest reaing
expected?
Quarterly i check
to'he conducted
a0%-80%

of range or near
norml reacing
expected?
Quartely igh check
to'he condcted
B0%-100%

of range, or igher
than highest rescing
since las test?

Thermasouples
calkrated using
NISTIASTM
proceures

or Ritype or Stype
used?
Annualreetive
accuracy test audt to
e conducted on al
mentoring systems
per Phase I Section
of CEM Manual?

Calbration gases
prepared per EPA
Traceatity Protocol?

Muticomponent
gases free from
interfererts.

and non-reactive?

Yes

Yes

Yes

Yes

Yes

Yes

Yeos

Yeos

Yes

Yes





[image: image52.jpg]Calioration gases for
maritors wit rticsl

orfices

approxinate soric

velocty of fue gases [Ves =
or approved

aternative

compensation

procedure used?

Zero gasesin

accordance wih 04 [Ves =

Section of CEMM?

Publishe F-factors
used?

=3 E

Fuel
sampingianalysisto [Ves E
deterrine F-factors?

F-tactors for non-

uriform fuels

determined Yes <
per QA Section of

cemz

QA per 40 CFR 75,
AppendxD, 215,58
il subperagraphs?
(o fuel fow
meters included in
systems, enter No)
Recards of manual
adustments. Yes =
maintaines?

Yos g

Recard of changes to
"K.factors” or

ather constants
maitained?

Commerts:

Reason for Initial Submittal B

Infarmation

Change: 7|
==

P4 Dept. of Environmental Protection DEP Home | CEM Home | Contack | Help | Logaut

For assistance, please call DEP at (717) 7053768
between the hours of £:00 AM to 430 PM or send an e-mail to
ep-efactshelpdeskteam@state. pa.

. |





	Field Label/Link
	Activity

	View Notes
	Clicking the View Notes link opens the View Notes page, which allows you to view all notes associated with this item.

Note:  This link is active only in the online CEMDPS application.  

	Add Note
	Clicking the Add Note link opens the Add Note page, which allows you to enter a note for this item.

Note:  This link is active only in the online CEMDPS application.  

	Effective Date
	Enter the effective date of the submitted information in the format mm/dd/yyyy or click the calendar icon to select a date from a calendar.  (See Date Selection for information on using the calendar to choose a date.)

	Data validation to comply with QA Section of CEM Manual (CEMM)?
	Use the drop-down list to answer Yes, No, or Not Applicable.

	PDF file containing QA Plan
	Click the Browse button to select a file to attach to the monitoring plan information.  The file you choose displays in the text box.  If you previously attached a file, the file name displays as a link.  Click on the file name link to view the previous attachment.

	Data reduction to comply with QA Section of CEMM?
	Use the drop-down list to answer Yes, No, or Not Applicable.

	Cal error checks to be conducted prior to maintenance if possible?
	Use the drop-down list to answer Yes, No, or Not Applicable.

	Cal error checks to be conducted following maintenance?
	Use the drop-down list to answer Yes, No, or Not Applicable.

	Linearity test to be conducted if post-maintenance checks exceed twice performance specification?
	Use the drop-down list to answer Yes, No, or Not Applicable.

	Daily zero and cal to be conducted on all measurement device ranges?
	Use the drop-down list to answer Yes, No, or Not Applicable.

	Reference material/signal to be applied as close to sample acquisition point as possible?
	Use the drop-down list to answer Yes, No, or Not Applicable.

	Measurement devices to be adjusted if cal error performance specifications exceeded?
	Use the drop-down list to answer Yes, No, or Not Applicable.

	Daily zero check to be conducted at 0%-30% of range or lower than lowest reading expected?
	Use the drop-down list to answer Yes, No, or Not Applicable.

	Daily cal check to be conducted at 40%-100% of range or near normal reading expected?
	Use the drop-down list to answer Yes, No, or Not Applicable.

	Quarterly linearity to be conducted on all measurement device ranges?
	Use the drop-down list to answer Yes, No, or Not Applicable.

	Quarterly low check to be conducted at 0%-30% of range or lower than lowest reading expected?
	Use the drop-down list to answer Yes, No, or Not Applicable.

	Quarterly mid check to be conducted at 40%-60% of range or near normal reading expected?
	Use the drop-down list to answer Yes, No, or Not Applicable.

	Quarterly high check to be conducted at 80%-100% of range, or higher than highest reading since last test?
	Use the drop-down list to answer Yes, No, or Not Applicable.

	Thermocouples calibrated using NIST/ASTM procedures or R-type or S-type used?
	Use the drop-down list to answer Yes, No, or Not Applicable.

	Annual relative accuracy test audit to be conducted on all monitoring systems per Phase II Section of CEM Manual?
	Use the drop-down list to answer Yes, No, or Not Applicable.

	Calibration gases prepared per EPA Traceability Protocol?
	Use the drop-down list to answer Yes, No, or Not Applicable.

	Multicomponent gases free from interferents and non-reactive?
	Use the drop-down list to answer Yes, No, or Not Applicable.

	Calibration gases for monitors with critical orifices approximate sonic velocity of flue gases or approved alternative compensation procedure used?
	Use the drop-down list to answer Yes, No, or Not Applicable.

	Zero gases in accordance with QA Section of CEMM?
	Use the drop-down list to answer Yes, No, or Not Applicable.

	Published F-factors used?
	Use the drop-down list to answer Yes, No, or Not Applicable.

	Fuel sampling/analysis to determine F-factors?
	Use the drop-down list to answer Yes, No, or Not Applicable.

	F-factors for non-uniform fuels determined per QA Section of CEMM?
	Use the drop-down list to answer Yes, No, or Not Applicable.

	QA per 40 CFR 75, Appendix D, 2.1.6, & all subparagraphs (if no fuel flow meters included in systems, enter No)?
	Use the drop-down list to answer Yes, No, or Not Applicable.

	Records of manual adjustments maintained?
	Use the drop-down list to answer Yes, No, or Not Applicable.

	Record of changes to “K-factors” or other constants maintained?
	Use the drop-down list to answer Yes, No, or Not Applicable.



	Comments
	Enter up to 125 characters of comments.

	Reason for Information Change
	Enter a reason for the information change up to 50 characters.


	Button
	Description

	Save
	Clicking Save saves the information and returns you to the Monitoring Plan page.

	Cancel
	Clicking Cancel returns you to the Monitoring Plan page without saving changes.


Configuration Information

Source Combinations

 XE "Type " \* MERGEFORMAT 

 XE "Status " \* MERGEFORMAT 

 XE "Source Combination " \* MERGEFORMAT 

 XE "Emission Result " \* MERGEFORMAT 

 XE "EDR 812 " \* MERGEFORMAT 

 XE "CEMSID " \* MERGEFORMAT 

 XE "Add Source Combination " \* MERGEFORMAT 

 XE "Add " \* MERGEFORMAT Add Source Combination

When you create a new monitoring plan and add source combinations, the Add Source Combination page displays.  This page contains a list of source combinations already defined for your facility and available for inclusion in your new monitoring plan.  If you do not have any source combinations defined for other monitoring plans for your facility, the Create Source Combination page displays instead and allows you to define a new source combination.

To add a source combination from the Add Source Combination page's list of defined combinations, click the radio button in front of the combination you want to add or click the button in front of the Add New Source Combination option and click Add.

[image: image53.jpg]‘Commonwealth of Pennsylvania

Bureau of Air Quality

- !
CEMDPS . ‘Department of Environmental Protection

Home ~~> Edit Monitoring Plan ~-> Add Source Cambination

Add Source Combination

- Create Synchvonization Fes

pr——
e
Y AR bR Add SotsEe. Emission Result CEMSID Type Status.
e comammies
w0127 00090 SR
Fom htUseR Opacty % 55 pRMARY  Cotedanorazoor
| To: EXTUSER el T
Opacty % 0o PRMARY oo
2005127099990
From: INTUSER unit 12
To: EXTUSER NOX IbsMBtU 528 BACKUP  Certfied on 08/28/2007
Thie e 8 orow sitiels NOx IhsMBtu 8249 PRIMARY Certified on 06/29/2007
w2
WO benEt so BAGNP  Cotdonornazont
O et w05 pRMARY  Cotdonorazooy
_—
&l unt12
et @ BAOAP  Cofedononzazno
N betEt 20 PRMARY  Cotidonoazazoo
B e
oot @2 eaoeP  Cotedonountzno
O betEt @55 PRMARY  Cotdonosntzno
f e
Opacty % o PRMARY oo
Opacty % o7 BAOAP oot
Opacty % s PRMARY oo
[T





	Column
	Activity

	Add
	Click the radio button in this column to select a source combination to add to your monitoring plan, or click the radio button for Add New Source Combination to define a new combination.

	Source Combination
	Displays the names of the source combinations already defined in the CEMDPS.

	Emission Result
	Displays the emission results associated with a source combination.

	CEMSID
	Displays the CEMS IDs associated with an emission result.

	Type
	Indicates whether the CEMS is the primary, backup, or standby.

	Status
	Indicates the status of the CEMS.


	Button
	Description

	Add
	Clicking this button adds the source combination selected in the Add column to the monitoring plan.


 XE "Reason for Information Change " \* MERGEFORMAT 

 XE "Rated Capacity " \* MERGEFORMAT 

 XE "Plan Approval Number " \* MERGEFORMAT 

 XE "Name " \* MERGEFORMAT 

 XE "Effective Date " \* MERGEFORMAT 

 XE "EDR 812 " \* MERGEFORMAT 

 XE "Create/Edit Source Combination " \* MERGEFORMAT 

 XE "Capacity Information Source " \* MERGEFORMAT Create/Edit Source Combination (EDR 812)
The Create/Edit Source Combination page records information about source combinations for a facility. (You get to this page by clicking Add next to the Source Combinations heading or Edit next to a source combination’s Basic Information in the Monitoring Plan page.)  A source combination consists of one or more processes (emissions from multiple processes are sometimes combined prior to monitoring) from which emissions or operational parameters are monitored to determine compliance with applicable emission standards or operational criteria. 

Notes 

· Each source combination must be associated with one and only one facility.

· Each source combination must have one or more emission results.

To add or edit a Source Combination, follow the instructions for each field, as listed below.  
[image: image54.jpg]Correspondence

- Send Message
- View AllMessages

2008-11-27 00:00:000
From: NTUSER
To: EXTUSER

2008-11-27 00:00:000
From: INTUSER.
To: EXTUSER

| s 3onger subject

ommonwealth of Pennsylvania

mrgmcuon

“EMDPS,_ - oosmrin

Bureau of Air

Home ~-> it Manitaing Plan --> Ect Source Cambination

Edit Source Coml

DR 012

View Notes | Ad Note

Effective Date:
Neme:

Plan Approval
Numer:

Rated Capacty:

02282001

| st v maniaayyyy)

i §

599940

oo

MBtuhr ] (Formet 29993399.99)

Capacty nformation [Records of Nanufacturer 5|

Source: =

Ressonfcr Tnitial Submittal A

Infarmation

Change: =
Save | [ Cancel

P4 Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout]

For assistance, please call DEP at (T17) 7053768
between the hours of £:00 AM to 430 PM or send an e-mail to
ep-efactshelpdeskteam@state. paus.





	Field Label/Link
	Activity

	View Notes
	Clicking the View Notes link opens the View Notes page, which allows you to view all notes associated with this item.

Note:  This link is active only in the online CEMDPS application.  

	Add Note
	ADD:  Clicking the Add Note link opens the Add Note page, which allows you to enter a note for this item.

Note:  This link is active only in the online CEMDPS application.  

	Effective Date
	Enter the effective date of the information in mm/dd/yyyy format or click the calendar icon to select a date from a calendar.  (See Date Selection for information on using the calendar to choose a date.)

	Name
	Enter the name for the source combination.

	Plan Approval Number
	Enter the DEP Plan Approval Number for the source combination (the number may be obtained from the DEP) in the format CC-SSS-NN, where:

CC = County number

SSS = Source Type Code

NN = Sequential Number.

	Rated Capacity
	Enter the Rated Capacity in F12.2 format and use the drop-down list to select the units of measurement for the Rated Capacity. The drop-down list contains the valid values for this field.  If the value you need is not in the drop-down list, please contact the DEP to request that a new value be added.

Examples of acceptable values are:

· ACFM

· bbl/day

· tons/hr

· lbs/day

· tons/yr

· lbs/hr

· Mbtu/hr

· tons/cycle



	Capacity Information Source
	Enter a short explanation of the source of the information (Manufacturer’s Rating, Test Results, etc.).

	Reason for Information Change
	Enter a reason for information change up to 50 characters. Before you submit the monitoring plan for the first time, the default text in this text box is Initial Submittal and it is not editable.  


	Button
	Description

	Save
	Clicking Save saves the information and returns you to the Monitoring Plan page.

	Cancel
	Clicking Cancel returns you to the Monitoring Plan page without saving changes.


 XE "Type of nearest upstream disturbance " \* MERGEFORMAT 

 XE "Type of nearest pollution control equipment " \* MERGEFORMAT 

 XE "Type of nearest downstream disturbance " \* MERGEFORMAT 

 XE "Reason for Information Change " \* MERGEFORMAT 

 XE "Location of pollution control equipment relative to MSML " \* MERGEFORMAT 

 XE "Flow Diagram Attachment " \* MERGEFORMAT 

 XE "Equivalent diameter of the flue at the monitoring system measurement location (MSML) " \* MERGEFORMAT 

 XE "Equipment Params Attachment " \* MERGEFORMAT 

 XE "Equipment Names Attachment " \* MERGEFORMAT 

 XE "Effective Date " \* MERGEFORMAT 

 XE "EDR 843 " \* MERGEFORMAT 

 XE "Edit General Monitoring Plan Information " \* MERGEFORMAT 

 XE "Distance of nearest upstream disturbance to MSML " \* MERGEFORMAT 

 XE "Distance of nearest pollution control equipment to MSML " \* MERGEFORMAT 

 XE "Distance of nearest downstream disturbance to MSML " \* MERGEFORMAT 

 XE "Distance of flue walls from sample acquisition point " \* MERGEFORMAT 

 XE "Distance of emission point of monitoring gases to MSML " \* MERGEFORMAT 

 XE "Comments " \* MERGEFORMAT Edit General Monitoring Plan Information (EDR 843)
The Create/Edit General Monitoring Plan Information page records general information about the monitoring plan, including locations of disturbances and pollution control equipment relative to the monitoring system measurement location (MSML).  You must enter this general information with each monitoring plan for a facility.
To add or edit General Monitoring Plan Information, follow the instructions for each field, as listed below.  
[image: image55.jpg]Commonwealth of Pennsylvania

CEMDPS ent of Environmental Protection
-

Bureau of Air Quality
e Home -~ Ect Mortring Plan - Edit Genersl Montoring Plan nformation
Edit General Monitoring Plan Information
_—— DR 043
| comespondence
| ~Send vessage View tstes | ad Note
|- View Al essages
——| 02282007 (must be manidaiyyy)
2006-11-27 0000000 et i di e (fommet 9399)
fron NI atthe montoring
1o xTuseR system
‘ = messuremertlocation
|| (e
TG e
From: NTUSER
wstream Ebow =]
iTa ExtusER dtutance:
| i s 3 nger subect Distance of earest [T | fest (format 3399)
ustream
lturbance to MSL:
Type of nearest
downstream Fan =]
dturbance:
Oitonce ofnearest [1 | fee format 5908)
downstream

disturbance to MSML:
Type of nesrest

pollton cortrol Cyo

ectipmen:

Distance of nesrest et ot 3559)

polltion cortrol
ectipment to MSML:

Location of poltion

controlequipment  [Downstream v

relative to MSHL:

Distance of emisson et ot 3559)

pairt o manitoring
gases to MSML

Distance o e wals et format 5355)

from sample
acauistion poirt:

et — o T
el e— o T

e
Atachmert Test_Dosument pa
Comments General 275 B

Reason for Tnitial Submittal 2

Infarmation

Chnge: =

Commerts:

A Dept. of Enviranmantsl Protection DEP Home | CEM Home | Contacts | Help | Logout]

For assistance, please call DEP at (717) 705-3768
between the hours of £:00 AM to 430 PM or send an e-mail to
ep-efactshelpdeskteam@state. pa.us.





	Field Label/Link
	Activity

	View Notes
	Clicking the View Notes link opens the View Notes page, which allows you to view all notes associated with this item.

Note:  This link is active only in the online CEMDPS application. 

	Add Note
	Clicking the Add Note link opens the Add Note page, which allows you to enter a note for this item.

Note:  This link is active only in the online CEMDPS application.  

	Effective Date
	Enter the effective date of the information in mm/dd/yyyy format or click the calendar icon to select a date from a calendar.  (See Date Selection for information on using the calendar to choose a date.)

	Equivalent diameter of the flue at the monitoring system measurement location (MSML):
	Enter the equivalent diameter of the flue at the monitoring system measurement location in feet in F4.1 format. 

	Type of nearest upstream disturbance:
	Use the drop-down list to enter the type of nearest upstream disturbance. The drop-down list contains the valid values for this field.  If the value you need is not in the drop-down list, please contact the DEP to request that a new value be added.

Examples of acceptable values are:

· Fan

· Elbow

· Inlet

· Outlet



	Distance of nearest upstream disturbance to MSML:
	Enter the distance of nearest upstream disturbance to MSML in feet in F4.1 format.

	Type of nearest downstream disturbance:
	Use the drop-down list to enter the type of nearest downstream disturbance. The drop-down list contains the valid values for this field.  If the value you need is not in the drop-down list, please contact the DEP to request that a new value be added.

Examples of acceptable values are:

· Fan

· Elbow

· Inlet

· Outlet



	Distance of nearest downstream disturbance to MSML:
	Enter the distance of nearest downstream disturbance to MSML in feet in F4.1 format. 

	Type of nearest pollution control equipment:
	Use the drop-down list to enter the type of nearest pollution control equipment. The drop-down list contains the valid values for this field.  If the value you need is not in the drop-down list, please contact the DEP to request that a new value be added.

Examples of acceptable values are:

Value

Description

B

Baghouse(s)

C

Cyclone

CM

Combustion Modification/Fuel Reburning

DA

Dual Alkali

DL

Dry Lime FGD

DLNB

Dry Low NOx Burners (Turbines only)

ESP

Electrostatic Precipitator

FBL

Fluidized Bed Limestone Injection

H2O

Water Injection (Turbines and Cyclone Boilers only)

LNB

Low NOx Burner Technology (Dry Bottom Boilers only)

LNBO

Low NOx Burner Technology with Overfire Air (Dry Bottom Boilers Only)

LNC1

Low NOx Burner Technology with Close-coupled OFA (Tangentially fired units only)

LNC2

Low NOx Burner Technology with Separated OFA (Tangentially fired units only)

LNC3

Low NOx Burner Technology with Close-coupled and Separated OFA (Tangentially fired units only)

LNCB

Low NOx Burner Technology for Cell Burners

MO

Magnesium Oxide

NH3

Ammonia Injection

O

Other

OFA

Overfire Air

SB

Sodium Based

SCR

Selective Catalytic Reduction

SNCR

Selective Non-catalytic Reduction

SO2

Controls

STM

Steam Injection

WL

Wet Lime FGD

WLS

Wet Limestone

WS

Wet Scrubber



	Distance of nearest pollution control equipment to MSML:
	Enter the distance of nearest pollution control equipment to MSML in feet in F4.1 format.

	Location of pollution control equipment relative to MSML:
	Use the drop-down list to report whether the location of pollution control equipment relative to the MSML is Upstream or Downstream.

	Distance of emission point of monitoring gases to MSML:
	Enter the distance of emission point of monitoring gases to the MSML in feet in F4.1 format. 

	Distance of flue walls from sample acquisition point:
	Enter the distance of flue walls from the sample acquisition point in feet.

	Equipment Names Attachment
	Click the Browse button to select a file to attach to the monitoring plan information.  The file you choose displays in the text box.  If you previously attached a file, the file name displays as a link.  Click on the file name link to view the previous attachment.

	Equipment Params Attachment
	Click the Browse button to select a file to attach to the monitoring plan information.   The file you choose displays in the text box.  If you previously attached a file, the file name displays as a link.  Click on the file name link to view the previous attachment.

	Flow Diagram Attachment
	Click the Browse button to select a file to attach to the monitoring plan information.   The file you choose displays in the text box.  If you previously attached a file, the file name displays as a link.  Click on the file name link to view the previous attachment.

	Comments
	Enter up to 40 characters of comments.

	Reason for Information Change
	Enter a reason for information change up to 50 characters.  Before you submit the monitoring plan for the first time, the default text in this text box is Initial Submittal and it is not editable.  


	Button
	Description

	Save
	Clicking Save saves the information and returns you to the Monitoring Plan page.

	Cancel
	Clicking Cancel returns you to the Monitoring Plan page without saving changes.


Emission Results

 XE "Units of Measurement " \* MERGEFORMAT 

 XE "Reason for Information Change " \* MERGEFORMAT 

 XE "Parameter/Pollutant " \* MERGEFORMAT 

 XE "Effective Date " \* MERGEFORMAT 

 XE "EDR 820 " \* MERGEFORMAT 

 XE "Data Substitution Required " \* MERGEFORMAT 

 XE "Create/Edit Emission Result " \* MERGEFORMAT 

 XE "Corrected To " \* MERGEFORMAT 

 XE "Basis of Measurement " \* MERGEFORMAT Create/Edit Emission Result (EDR 820)
The Create/Edit Emission Result page records information about emission results for source combinations.  An emission result represents data in terms of an applicable emission standard or operational criterion as reported to BAQ.

Notes

· Each emission result must be associated with one and only one source combination.

· Each emission result must have one or more emission standards (if emissions are being reported for informational purposes only, the emission standard parameters can be set such that compliance is not determined), one or more data availability standards (if emissions are being reported for informational purposes only, the data availability standard parameters can be set such that compliance is not determined), and one or more (to account for “backup” or “standby” monitoring systems used to collect and report data for the same emission result) continuous emission monitoring systems (CEMSs).

To add or edit an Emission Result, follow the instructions for each field, as listed below.  

[image: image56.jpg]~ Commonwealth of Pennsylvania
ent of Environmental Protection I’
Bureau of Air Quality

- Send Message
- View AllMessages

| 2008-11-27 0000000
| From WTUSER

To: EXTUSER
|2008-11-27 0000000
From: NTUSER

To: EXTUSER

his 5 3 ongersubject

Home ~-> Edt Manitoing Plan ~-> Ect Emission Result

Edit Emission Result
DR 020

View Notes | Ad Note

Effective Date: 02282007 (st be munidayyyy)
Parameterolitart:  [Opacty <

Unisof |
Measurement: kd e
e v |
Corestetto =

Dta Substiution
Recurect o =]

Reason for
R Initial Submittal
Change:

[save]

P Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (T17) 7053768
between the hours of £:00 AM to 430 PM or send an e-mailto
ep-efactshelpdeskteam@state.pa.us.





	Field Label/Link
	Activity

	View Notes
	Clicking the View Notes link opens the View Notes page, which allows you to view all notes associated with this item.

Note:  This link is active only in the online CEMDPS application.  

	Add Note
	Clicking the Add Note link opens the Add Note page, which allows you to enter a note for this item.

Note:  This link is active only in the online CEMDPS application.  

	Effective Date
	Enter the effective date of the information in mm/dd/yyyy format or click the calendar icon to select a date from a calendar.  (See Date Selection for information on using the calendar to choose a date.)

	Parameter/Pollutant
	Use the drop-down list to enter the Parameter/Pollutant for the emission result. The drop-down list contains the valid values for this field.  If the value you need is not in the drop-down list, please contact the DEP to request that a new value be added.

Examples of acceptable values are:

CE

CO 

CO2 

Culm Gas %

Flow

Fuel Rate

H2O 

H2S

HC 

HCl 

HCl Reduction

Heat Input 

NO 

NO2 

NOx 

NOx Allowable

O2 

Opacity 

Pressure 

SO2
SO2 Allowable 

SO2 Reduction 

Steam Flow

Temperature

TRS 

VCM 

VOC 



	Units of Measurement
	Use the drop-down list to enter the Units of Measurement for the emission result. The drop-down list contains the valid values for this field.  If the value you need is not in the drop-down list, please contact the DEP to request that a new value be added.

Examples of acceptable values are:

%

Btu/hr 

cfh 

Cfm

Degrees F

gph 

gpm 

lbs/hr

lbs/Mbtu

lbs/ton

Mbtu/hr 

Mcfh

ppm 

psi 



	Basis of Measurement
	Use the drop-down list to enter the Basis of Measurement for the emission result. The drop-down list contains the valid values for this field.  If the value you need is not in the drop-down list, please contact the DEP to request that a new value be added.

Examples of acceptable values are:

· Wet (W)

· Dry (D)

· Not Applicable (N)

	Corrected To
	Use the drop-down list to enter the Corrected To value for the emission result. The drop-down list contains the valid values for this field.  If the value you need is not in the drop-down list, please contact the DEP to request that a new value be added.

Examples of acceptable values are:

· **  (Not Applicable)

· 0% O2

· 10% O2

· 12% O2

· 15% O2

· 7% O2

· 8% O2

	Data Substitution Required
	Use the drop-down list to enter whether data substitution is required.  Acceptable values are:

· Yes - Data substitution required when data invalid

· No - Data substitution not required

	Reason for Information Change
	Enter a reason for information change up to 50 characters. Before you submit the monitoring plan for the first time, the default text in this text box is Initial Submittal and it is not editable.  


	Button
	Description

	Save
	Clicking Save saves the information and returns you to the Monitoring Plan page. 

	Cancel
	Clicking Cancel returns you to the  Monitoring Plan page without saving changes.


 XE "Regulatory Citation " \* MERGEFORMAT 

 XE "Reason for Installation " \* MERGEFORMAT 

 XE "EDR 821 " \* MERGEFORMAT Emission Result Reasons (EDR 821)

The Emission Result Reasons page displays a list of emission result reasons already configured for an emission result.  The page title includes the name of the emission result associated with the reasons listed.  For example, when you view the emission result reasons for an emission result called "Fuel Rate Btu/hr," the page title is Emission Result Reasons for Fuel Rate Btu/hr.  From the Emission Result Reasons page, you can add a new reason for the emission result or edit or remove an existing reason.

The table below describes the information displayed in the Emission Result Reasons page and the options available. 

[image: image57.jpg]~ Commonwealth of Pennsylvania
ent of Environmental Protection I’
Bureau of Air Quality

Home ~-> it Manitoing Plan ~-> Ect Emission Result Reasons

Emission Result Reasons for

_ Opacity % &
[_comeerontorss | e

frstrams

ViR M Weiones Reason for Installation Regulatory Citation

[ me ] PLAN Approval Ciaton 1

| 2006-11-27 om.0m008

o nrusew |

o xTusER

| 2008-11-27 000000
From: INTUSER.

| s 3 onger subjet

A Dept. of Enviranmantal Protection DEP Home | CEM Home | Contacts | Help | Logout]

For assistance, please call DEP at (T17) 7053768
between the hours of £:00 AM to 430 PM or send an e-mailto
ep-efactshelpdeskteam@state.pa.us.





	Column
	Description

	Reason for Installation
	Displays the reason for installation for the emission result reason.

	Regulatory Citation
	Displays the regulatory citation for the reason for installation.


	Button
	Description

	Add
	Click Add to enter a new emission result reason for the emission result.  The Create Emission Result Reason  page displays.

	Edit
	Click Edit next to the appropriate emission result reason to make changes to that reason.  The Edit Emission Result Reason page displays.

	Remove
	Click Remove next to the appropriate emission result reason to remove it from the reasons list. Clicking this link opens the Delete <Item> page, which allows you to confirm or cancel the deletion.


 XE "Regulatory Citation " \* MERGEFORMAT 

 XE "Reason for Installation " \* MERGEFORMAT 

 XE "Reason for Information Change " \* MERGEFORMAT 

 XE "Effective Date " \* MERGEFORMAT 

 XE "EDR 821 " \* MERGEFORMAT 

 XE "Create/Edit Emission Result Reason " \* MERGEFORMAT Create/Edit Emission Result Reason (EDR 821)
The Create/Edit Emission Result Reason page records information regarding the reasons for why monitoring is required for each existing or proposed new emission result at a facility.  You may enter up to 5 reasons per emission result.
To add or edit an Emission Result Reason, follow the instructions for each field, as listed below.  
[image: image58.jpg]~ Commonwealth of Pennsylvania
ent of Environmental Protection T
Bureau of Air Quality

Home ~> Edt Manitoring Plan ~-> Enission Result Reasans List ~-> EdRt Emission Resut Reason

Edit Emission Result Reason

DR 821

“Send essage View Notes | Ad Note
- View AllMessages

[ wbox || cretveome 02282007 (st be manidayyyy)
Reason for

2008-11-27 00:00:000 roval v
Instalitio: Blailbe

From: INTUSER

To: EXTUSER Restory Ctoion:[C1E8E108 1 —H

s I |

2008-11-27 00:00:000 Ressch o Initial Submittal =

From: INTUSER Change: i

[ — ==

A Dept. of Enviranmantal Protection DEP Home | CEM Home | Contacts | Help | Logout]

For assistance, please call DEP at (717) 7053768
between the hours of £:00 AM to 430 PM or send an e-mail to
ep-efactshelpdeskteam@state. pa.us.





	Field Label/Link
	Activity

	View Notes
	Clicking the View Notes link opens the View Notes page, which allows you to view all notes associated with this item.

Note:  This link is active only in the online CEMDPS application.    

	Add Note
	Clicking the Add Note link opens the Add Note page, which allows you to enter a note for this item.

Note:  This link is active only in the online CEMDPS application.

	Effective Date
	Enter the effective date of the information in mm/dd/yyyy format or click the calendar con to select a date from a calendar.  (See Date Selection for information on using the calendar to choose a date.)

	Reason for Installation
	Use the drop-down list to enter the Reason for Installation. The drop-down list contains the valid values for this field.  If the value you need is not in the drop-down list, please contact the DEP to request that a new value be added.

Examples of acceptable values are:

Value

Description

**

Not Applicable

?

Unknown

Ne

NESHAPS

Ns

NSPS

O

Department Order

P1

Acid Rain Phase I

P2

Acid Rain Phase II

Pa

Plan Approval

Ps

PSD

R

RACT

S

SIP

T

Trading Program



	Regulatory Citation
	Enter the regulatory citation for the reason represented by the Reason for Installation (for instance, “25 PA Code - Chapter 127”, “25 PA Code – Chapter 145”, etc.).

	Reason for Information Change
	Enter a reason for information change up to 50 characters. Before you submit the monitoring plan for the first time, the default text in this text box is Initial Submittal and it is not editable.  


	Button
	Description

	Save
	Clicking Save saves the information and returns you to the Emission Result Reasons page. 

	Cancel
	Clicking Cancel returns you to the Emission Result Reasons page without saving changes.


 XE "Start Date " \* MERGEFORMAT 

 XE "End Date " \* MERGEFORMAT 

 XE "Emission Standard Config " \* MERGEFORMAT 

 XE "EDR 822 " \* MERGEFORMAT Emission Standards (EDR 822)

The Emission Standards page displays a list of emission standards already configured for an emission result.  The page title includes the name of the emission result associated with the standards listed.  For example, when you view the emission standards for an emission result called "Fuel Rate Btu/hr," the page title is Emission Standards for Fuel Rate Btu/hr.  From the Emission Standards page, you can add a new standard for the emission result or edit or remove an existing standard.

The table below describes the information displayed in the Emission Standards page and the options available. 

[image: image59.jpg]~ Commonwealth of Pennsylvania
ent of Environmental Protection I’
Bureau of Air Quality

- Send Message
- View AllMessages

| 2006-11-27 om.0m008
 From: NTUSER
o xTusER

| 2008-11-27 000000
From: INTUSER.

| s 3 onger subjet

Home ~~> Edit Manitring Plan ~-> Edt Emission Standrds

Emission Standards for
Opacity %

DR 022

Emission Standard Config Startdate _End date

2ot average, rolig by 1 mertn 07202007 001472007

P Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (T17) 7053768
between the hours of £:00 AM to 430 PM or send an e-mailto
ep-efactshelpdeskteam@state.pa.us.





	Column
	Description

	Emission Standard Config
	Displays a list of emission standards configured for an emission result.

	Start Date
	Displays the starting date the standard applies.

	End Date
	Displays the last date the standard applies.


	Button
	Description

	Add
	Click Add to enter a new emission standard. The Create Emission Standard Information page displays.

	Edit
	Click Edit next to the appropriate emission standard to make changes to that standard.  The Edit Emission Standard Information page displays.

	Remove
	Click Remove next to the appropriate emission standard to remove it from the standards list. Clicking this link opens the Delete <Item> page, which allows you to confirm or cancel the deletion.


 XE "Variable Emission Result ID Code " \* MERGEFORMAT 

 XE "Truncation Level " \* MERGEFORMAT 

 XE "Start Date " \* MERGEFORMAT 

 XE "Reason for Information Change " \* MERGEFORMAT 

 XE "Penalty Parameter " \* MERGEFORMAT 

 XE "Or'd Emission Standard ID Code " \* MERGEFORMAT 

 XE "Or'd Emission Result ID Code " \* MERGEFORMAT 

 XE "End Date " \* MERGEFORMAT 

 XE "Emission Standard Value " \* MERGEFORMAT 

 XE "Emission Standard ID Code " \* MERGEFORMAT 

 XE "Emission Standard Direction " \* MERGEFORMAT 

 XE "EDR 822 " \* MERGEFORMAT 

 XE "Create/Edit Emission Standard Information " \* MERGEFORMAT 

 XE "And/Or Standard (for or'd Standards) " \* MERGEFORMAT Create/Edit Emission Standard Information (EDR 822)

The Create/Edit Emission Standard Information page records information about emission standards for emission results at a facility.  
To add or edit an Emission Standard, follow the instructions for each field, as listed below.  
[image: image60.jpg]ommonwealth of Pennsylvania

EEMDPS B it

Bureau of Air.

- Send Message
- View AllMessages

 From mTuser

}Ta extuseR
2005.11.27 0000000
|From: mTUSER

1o UsER

| s 3onger subject

-

Home ~-> it Manitaing Plan ~-> Ect Emission Standard nformation

Edit Emission Standard Information

DR 022

View Notes | Ad Note

Enission Standard D
Code:

Stort Date:

End Date:
Enission Standard
Value:

Variable Emission
Resut D Cad:

Enission Standard
Directon:

Truncation Level:

Penaty Parameter
Ao Flag (for
"ord”Standarct):
Ord Enission Result
D Cack:

Ord Enission
Standerd ID Cod:
Reason for
Infarmation

Change:

[12-month average, rolling by 1 month

07282007 | st o memiaayyy)
fos 142007 = st o memiaayyy)
100 Format 339393099.99939
351

Loss Than |

0 Blog

[EMwisHowco =]
sl

Tnitial Submittal =

ED

Cancer|

P4 Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (T17) 7053763
between the hours of £:00 AM to 430 PM or send an e-mail to
ep-efactshelpdeskteam@state. pa.us.





	Field Label/Link
	Activity

	View Notes
	Clicking the View Notes link opens the View Notes page, which allows you to view all notes associated with this item.

Note:  This link is active only in the online CEMDPS application.   

	Add Note
	Clicking the Add Note link opens the Add Note page, which allows you to enter a note for this item.

Note:  This link is active only in the online CEMDPS application. 

	Emission Standard ID Code
	Use the drop-down list to enter the Emission Standard ID Code to identify the type of averaging/summation period involved. The drop-down list contains the valid values for this field.  If the value you need is not in the drop-down list, please contact the DEP to request that a new value be added.

Examples of acceptable values are:

No ESIDC (Use for DA Std Only)

Std1dev, no exceptions

1-Minute average, 3 exceptions in hour

Std2dev, no exceptions

1-Minute average, block

4-hour average, block

1-day average, block

12-hour average, block

Daily averages, 2 exceptions in 30-day

24-hour average, rolling by 1 hour

30-day average, rolling by 1 day

6-minute average, block

1-hour average, block

1-day sum

4-day average, rolling by 1 day

12-month sum, rolling by 1 month

3-hour average, rolling by 1 hour

12-month average, rolling by 1 month

4-hour average, rolling by 1 hour

3-hour average, block

8-hour average, rolling by 1 hour

7-day average, rolling by 1 day

12-hour average, rolling by 1 hour

1-day average, block, geometric

1-Year sum

30-Operating-Day operating hour average, by 1 day

Std1dev, 3 exceptions in hour

1-month average, block



	Start Date
	Enter the starting date the standard applies in mm/dd/yyyy format or click the calendar icon to select a date from a calendar.  (See Date Selection for information on using the calendar to choose a date.) 

	End Date
	Enter the last date the standard applies in mm/dd/yyyy format or click the calendar icon to select a date from a calendar.  (See Date Selection for information on using the calendar to choose a date.)   If standard is still applicable, report 12/31/9999.

	Emission Standard Value
	Enter the value of the emission standard.  If the emission result is subject to a “variable” standard (based on process operating conditions, etc.), leave this field blank.  Use format F16.6 for data entered in this field.

	Variable Emission Result ID Code
	Should the emission result be subject to a “variable” standard (based on process operating conditions, etc.), enter the DEP Emission Result ID Code for the emission result used to report such “variable” emission standard for comparison with the emission result represented by this record.  

	Emission Standard Direction
	Use the drop-down list to enter the Emission Standard Direction. Acceptable values are:

Less Than 

Violation if monitoring result is less than the emission standard value

Less Than Equal

Violation if monitoring result is less than or equal to the emission standard value

Greater Than

Violation if monitoring result is greater than the emission standard value

Greater Than Equal

Violation if monitoring result is greater than or equal to the emission standard value



	Truncation Level
	Enter the truncation level (as supplied by the PADEP).  Acceptable values are in the range “-6” to “+9”, with “+0” as a valid value.

	Penalty Parameter
	Use the drop-down list to enter the Penalty Parameter. The drop-down list contains the valid values for this field.  If the value you need is not in the drop-down list, please contact the DEP to request that a new value be added.

Examples of acceptable values are:

E-General 1-Month Ave

D-MWI Opacity

E-General 12-Month roll

E-Boiler/General 20% Standard Opacity

E-MWI CE

E-Boiler/General 60% Standard Opacity

D-Hospital Incinerator CE, CO, Temp.

E-Cement Kiln 20% Standard Opacity

D-MWI CE, CO, Temp.

E-Cement Kiln 60% Standard Opacity

E-Hospital Incinerator Daily CO

E-FCC 20% Standard Opacity

E-MWI 4 Day CO

E-FCC 60% Standard Opacity

E-MWI 4 Hour CO

E-FCC 20% Standard After October 2004 Opacity

E-MWI 8 Hour CO

E-FCC 60% Standard After October 2004 Opacity

E-MWI Daily CO

E-MWI 10% Standard Opacity

E-MWI Daily CO After ???

E-MWI 30% Standard Opacity

E-Interim Guidelines Hourly-Main Standards

E-MWI Daily SO2

E-MWI Daily HCl

E-MWI Hourly SO2

E-MWI Daily HCl After ???

E-Blr/G Daily (lbs/Mbtu, ppm, lbs/hr) SO2, NOx, CO

E-MWI Daily HCl no Reduction

E-Boiler/General 2-in-30 Day SO2, NOx, CO

E-Boiler Homer City Only NOx

E-Boiler/General 30-Day SO2, NOx, CO

E-MWI Daily NOx

E-Boiler/General Daily/30D (lbs/Mbtu) SO2, NOx, CO

D-Boiler/General Hourly Opacity

D-MWI SO2, NOx, HCl

D-Cement Kiln Opacity

D-Boiler/General Hourly, Daily SO2, NOx, TRS

D-FFC Opacity

E-Interim Guidelines Hourly - Temp. Adj Stds

D-FFC Opacity October 2004

E-MWI Minute Temp.



	And/Or Flag (for "or'd" Standards)
	Use the drop-down list to select And or Or.  If the emission standard applies in addition to any other emission standards (or is the only emission standard), select And.  If the emission standard is one of a number of alternatives, select Or.

	Or'd Emission Result ID Code
	If the emission standard is one of a number of alternatives, enter the emission result ID code to which the or’d standard applies. Otherwise, leave this field blank.

	Or'd Emission Standard ID Code
	If the emission standard is one of a number of alternatives, enter the emission standard ID code of the emission result ID code for the or’d standard which applies.  Otherwise, leave this field blank.

	Reason for Information Change
	Enter a reason for information change up to 50 characters. Before you submit the monitoring plan for the first time, the default text in this text box is Initial Submittal and it is not editable.  


	Button
	Description

	Save
	Clicking Save saves the information and returns you to the Emission Standards page. 

	Cancel
	Clicking Cancel returns you to the Emission Standards page without saving changes.


 XE "Start Date " \* MERGEFORMAT 

 XE "End Date " \* MERGEFORMAT 

 XE "EDR 823 " \* MERGEFORMAT 

 XE "Data Availability Standard Config " \* MERGEFORMAT Data Availability Standards (EDR 823)

The Data Availability Standards page displays a list of data availability standards already configured for an emission result.  The page title includes the name of the emission result associated with the standards listed.  For example, when you view the data availability standards for an emission result called "Fuel Rate Btu/hr," the page title is Data Availability Standards for Fuel Rate Btu/hr.  From the Data Availability Standards page, you can add a new data availability standard for the emission result or edit or remove an existing standard.

The table below describes the information displayed in the Data Availability Standards page and the options available. 

[image: image61.jpg]~ Commonwealth of Pennsylvania
ent of Environmental Protection I’
Bureau of Air Quality

- Send Message
- View AllMessages

| 2006-11-27 om.0m008
 From: NTUSER
o xTusER

| 2008-11-27 000000
From: INTUSER.

| s 3 onger subjet

Home ~-> Edt Manitoring Plan ~-> Edt Data avalabity Standards

Data Availability Standards for

Opacity %
DR 023
Data Availabilty Standard Config Startdate__End date
90% averages n merdh 28007

(|

P Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (T17) 7053768
between the hours of £:00 AM to 430 PM or send an e-mailto
ep-efactshelpdeskteam@state.pa.us.





	Column
	Description

	Data Availability Standard Config
	Displays a list of data availability standards configured for an emission result.

	Start Date
	Displays the starting date the standard applies.

	End Date
	Displays the last date the standard applies.


	Button
	Description

	Add
	Click Add to enter a new data availability standard. The Create Data Availability Standard Information page displays.

	Edit
	Click Edit next to the appropriate data availability standard to make changes to that standard.  The Edit Data Availability Standard Information page displays.

	Remove
	Click Remove next to the appropriate data availability standard to remove it from the standards list. Clicking this link opens the Delete <Item> page, which allows you to confirm or cancel the deletion.


 XE "Start Date " \* MERGEFORMAT 

 XE "Reason for Information Change " \* MERGEFORMAT 

 XE "End Date " \* MERGEFORMAT 

 XE "Emission Standard ID Code for or'd Standard " \* MERGEFORMAT 

 XE "Emission Standard ID Code " \* MERGEFORMAT 

 XE "EDR 823 " \* MERGEFORMAT 

 XE "Data Availability Standard ID Code for Or'd Standard " \* MERGEFORMAT 

 XE "Data Availability Standard ID Code " \* MERGEFORMAT 

 XE "Create/Edit Data Availability Standard Information " \* MERGEFORMAT 

 XE "And/Or Standard (for or'd Standards) " \* MERGEFORMAT Create/Edit Data Availability Standard Information (EDR 823)

The Create/Edit Data Availability Standard page records information about data availability standards for emission results at a facility.  You must enter at least one data availability standard for each emission result.
To add or edit a Data Availability Standard, follow the instructions for each field, as listed below.  
[image: image62.jpg]Commonwealth of Pennsylvania
ent of Environmental Protection P
> Bureau of Air Quality

- Send Message
- View AllMessages

Inbox
| 2006-11-27 om.0m008
| From: mTUSER
To EXTUSER
| 2006.11.27 om.00000

From: NTUSER
To EXTUSER

Home ~> Edit Manitoring Plan ~-> Edt Data awalabity Standard Informatian

Edit Data Availability Standard Information

DR 023

View Notes | Ad Note

his 5 3 ongersubject

Do vty o]
Stendrd D Code: |07 V130 )

St oate (st be mavitayyyy)
Endoete T

Enission Standard D
Code:

Andor Steerd for [——5]
or'd Standrds):
Enission Standard D

Code for Ord
Standard:

Deta Avalabitty

Standerd ID Code for =

Ord Standarct

Reason for Tnitial Submittal 2
Infarmation
Change: =

[save]

P4 Dept. of Emvironmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (717) 7053768
between the hours of £:00 AM to 430 PM or send an e-mail to
ep-efactshelpdeskteam@state.pa.us.





	Field Label/Link
	Activity

	View Notes
	Clicking the View Notes link opens the View Notes page, which allows you to view all notes associated with this item.

Note:  This link is active only in the online CEMDPS application.    

	Add Note
	Clicking the Add Note link opens the Add Note page, which allows you to enter a note for this item.

Note:  This link is active only in the online CEMDPS application.

	Data Availability Standard ID Code
	Use the drop-down list to enter the Data Availability Standard ID Code. The drop-down list contains the valid values for this field.  If the value you need is not in the drop-down list, please contact the DEP to request that a new value be added.

Examples of acceptable values are:

Value

Description

1

90% hours in month

2

95% hours in quarter

3

90% averages in month

4

75% averages in month

5

85% averages in quarter

6

100% hours in quarter

7

95% hours in day

8

50% hours in 30-day

9

23 days in 30-day

10

100% hours in day



	Start Date
	Enter the starting date the standard applies in mm/dd/yyyy format or click the calendar icon to select a date from a calendar.  (See Date Selection for information on using the calendar to choose a date.)

	End Date
	Enter the last date the standard applies in mm/dd/yyyy format or click the calendar icon to select a date from a calendar.  (See Date Selection for information on using the calendar to choose a date.) If the standard is still applicable, report 12/31/9999.

	Emission Standard ID Code
	Use the drop-down list to enter the Emission Standard ID Code.  If the Data Availability Standard is not related to an Emission standard, choose No ESIDC (Use for DA Std Only). The drop-down list contains the valid values for this field.  If the value you need is not in the drop-down list, please contact the DEP to request that a new value be added.

Examples of acceptable values are:

Value

Description

0

No ESIDC (Use for DA Std Only)

1

1-Minute average, 3 exceptions in hour

2

1-Minute average, block

3

1-day average, block

4

Daily averages, 2 exceptions in 30-day

5

30-day average, rolling by 1 day

6

1-hour average, block

7

4-day average, rolling by 1 day

8

3-hour average, rolling by 1 hour

9

4-hour average, rolling by 1 hour

10

8-hour average, rolling by 1 hour

11

12-hour average, rolling by 1 hour

12

1-Year sum

13

Std1dev, 3 exceptions in hour

14

Std1dev, no exceptions

15

Std2dev, no exceptions

16

4-hour average, block

17

12-hour average, block

18

24-hour average, rolling by 1 hour

19

6-minute average, block

20

1-day sum

21

12-month sum, rolling by 1 month

22

12-month average, rolling by 1 month

23

3-hour average, block

24

7-day average, rolling by 1 day

25

1-day average, block, geometric

26

30-Operating-Day operating hour average, by 1 day

27

1-month average, block



	And/Or Standard (for or'd Standards)
	Use the drop-down list to enter the And/Or Standard for or'd standards.  Acceptable values are:

· And (A) - The data availability standard applies in addition to any other data availability standards, or is the only data availability standard.

· Or (O) - The data availability standard is one of a number of alternatives

	Emission Standard ID Code for or'd Standard
	If the Emission Standard is one of a number of alternatives, use the drop-down list to enter the Emission Standard ID Code for Or'd Standard. The drop-down list contains the valid values for this field. If the value you need is not in the drop-down list, please contact the DEP to request that a new value be added.

Examples of acceptable values are:

Value

Description

0

No ESIDC (Use for DA Std Only)

1

1-Minute average, 3 exceptions in hour

2

1-Minute average, block

3

1-day average, block

4

Daily averages, 2 exceptions in 30-day

5

30-day average, rolling by 1 day

6

1-hour average, block

7

4-day average, rolling by 1 day

8

3-hour average, rolling by 1 hour

9

4-hour average, rolling by 1 hour

10

8-hour average, rolling by 1 hour

11

12-hour average, rolling by 1 hour

12

1-Year sum

13

Std1dev, 3 exceptions in hour

14

Std1dev, no exceptions

15

Std2dev, no exceptions

16

4-hour average, block

17

12-hour average, block

18

24-hour average, rolling by 1 hour

19

6-minute average, block

20

1-day sum

21

12-month sum, rolling by 1 month

22

12-month average, rolling by 1 month

23

3-hour average, block

24

7-day average, rolling by 1 day

25

1-day average, block, geometric

26

30-Operating-Day operating hour average, by 1 day

27

1-month average, block



	Data Availability Standard ID Code for Or'd Standard
	If the Data Availability Standard is one of a number of alternatives, use the drop-down list to enter the Data Availability Standard ID Code for Or'd Standard. The drop-down list contains the valid values for this field.  If the value you need is not in the drop-down list, please contact the DEP to request that a new value be added.

Examples of acceptable values are:

Value

Description

1

90% hours in month

2

95% hours in quarter

3

90% averages in month

4

75% averages in month

5

85% averages in quarter

6

100% hours in quarter

7

95% hours in day

8

50% hours in 30-day

9

23 days in 30-day

10

100% hours in day



	Reason for Information Change
	Enter a reason for information change up to 50 characters. Before you submit the monitoring plan for the first time, the default text in this text box is Initial Submittal and it is not editable.  


	Button
	Description

	Save
	Clicking Save saves the information and returns you to the Data Availability Standards page. 

	Cancel
	Clicking Cancel returns you to the Data Availability Standards page without saving changes.


CEMS

 XE "Type " \* MERGEFORMAT 

 XE "Reason for Information Change " \* MERGEFORMAT 

 XE "Opacity/Non-Opacity " \* MERGEFORMAT 

 XE "Effective Date " \* MERGEFORMAT 

 XE "EDR 824 " \* MERGEFORMAT 

 XE "Create/Edit CEMS " \* MERGEFORMAT 

 XE "CEM Manual Revision Number " \* MERGEFORMAT Create/Edit CEMS (EDR 824)
The Create/Edit CEMS page records information about CEMSs for each emission result at a facility.  A CEMS represents the monitoring system used to collect and report data for a particular emission result.  You must create at least one CEMS for each emission result.

Notes

· Each CEMS must be associated with one and only one emission result.

· Each CEMS must have one or more analyzers (measurement devices).

To add or edit a CEMS, follow the instructions for each field, as listed below.  
[image: image63.jpg]~ Commonwealth of Pennsylvania
ent of Environmental Protection
Bureau of Air Quality

- View AllMessages

| 2006-11-27 om.0m008
 From: NTUSER

To: EXTUSER
2008-11-27 00:00:000
From: INTUSER.

To: EXTUSER

his 5 3 ongersubject

- Send Message

Horme - Edit Moritoring Plan --> Edt CEMS

Edit CEMS

DR 024

View Notes | Ad Note

Effective Date: 02282007
Type: PRIMARY

CEMarua Reison
Nt O]
OpacityNon-Opacity. |Hon-Opacity v |
Resson for

e ,—_|Inma; Summizeal
Cronge

[Save]

(must be muniddyyyy)

P4 Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (717) 705-3768
between the hours of £:00 AM to 430 PM or send an e-mail to
ep-efactshelpdeskteam@state. pa.us.





	Field Label/Link
	Activity

	View Notes
	Clicking the View Notes link opens the View Notes page, which allows you to view all notes associated with this item.

Note:  This link is active only in the online CEMDPS application.  

	Add Note
	Clicking the Add Note link opens the Add Note page, which allows you to enter a note for this item.

Note:  This link is active only in the online CEMDPS application.  

	Effective Date
	Enter the effective date of the information in mm/dd/yyyy format or click the calendar con to select a date from a calendar.  (See Date Selection for information on using the calendar to choose a date.)

	Type
	Use the drop-down list to enter whether the CEMS is the Primary CEMS, or a Backup or Standby CEMS as follows:

Primary CEMS 

Only one Primary CEMS is allowed. Data from this CEMS must be reported unless they are invalid and other Standby or Backup CEMSs exist.

Standby CEMS

You may have one to 100 Standby CEMSs.  CEMSs must be installed and undergoing all normal operation and quality assurance requirements.  Data from Standby CEMSs may be used if the data from the Primary CEMS are invalid. Data from Standby CEMSs must be used from the first Standby CEMS with valid data in number order from lowest to highest.

Backup CEMS
You may have one to 100 Backup CEMSs.  Backup CEMSs are installed only when needed.  Quality assurance checks must be conducted prior to use of data from Backup CEMSs.  Data from Backup CEMSs may be used if the data from the Primary CEMS and all -- if any -- Standby CEMSs are invalid.  Data from Backup CEMSs must be used from the first Backup CEMS with valid data in number order from lowest to highest.

	CEM Manual Revision Number
	Use the drop-down list to enter the CEM Manual Revision Number under which the CEMS has obtained or is requesting approval.

	Opacity/Non-Opacity
	Use the drop-down list to enter whether the CEMS is for an Opacity or Non-Opacity analyzer. 

	Reason for Information Change
	Enter a reason for information change up to 50 characters. Before you submit the monitoring plan for the first time, the default text in this text box is Initial Submittal and it is not editable.  


	Button
	Description

	Save
	Clicking Save saves the information and returns you to the Monitoring Plan page. 

	Cancel
	Clicking Cancel returns you to the Monitoring Plan page without saving changes.


 XE "Time Without Corrective Maintenance " \* MERGEFORMAT 

 XE "Reason for Information Change " \* MERGEFORMAT 

 XE "Opacity Relative Accuracy, Average of 15 1-Minute Averages " \* MERGEFORMAT 

 XE "Opacity Relative Accuracy, 1-Minute Averages " \* MERGEFORMAT 

 XE "Effective Date " \* MERGEFORMAT 

 XE "EDR 834 " \* MERGEFORMAT 

 XE "DAS System Accuracy, 1-Minute Averages " \* MERGEFORMAT 

 XE "DAS System Accuracy, 1-Hour Averages " \* MERGEFORMAT 

 XE "Create/Edit Opacity CEMS Specification Information " \* MERGEFORMAT Create/Edit Opacity CEMS Specification Information (EDR 834)
The Create/Edit Opacity CEMS Specification Information page records information about opacity CEMSs.  You must enter specification information for each opacity CEMS at a facility.

To add or edit Opacity CEMS Specification Information, follow the instructions for each field, as listed below.  
[image: image64.jpg]Commonwealth of Pennsylvania

@MDPS@*s;:::::rm::&:’"""““ ;

Horme -~ Edit Moritorng Plan - Opacy CEMS Specificatio nformation

Quick Links.

| “Home

\cheas symaneirimaicEiss Edit Opacity CEMS Specification Information
Loty for Opacity % - PRIMARY

—nvnvrov
[ Correspondence EDR 834

B Visw Notes | Add Note.
- View AllMessages

mbox i E—] )
T Note it ollowing atues shoutd be 3> coimed by the manifactrer
| From: INTUSER ‘Time without
1o exTuseR criade [ hows Format sss)
| e Opacity Relative
20061127 ovo0000 fanle [ % romatsss
From WTuseR Tminde everoges:
7o BrusER Opacty Relstive
| this i a longer subject ke
| e ai1st. | %Famaisw
Tinte averages
DS System

s [ ooty ot 55559

1-minute averages:
Das System

P [ ooty romatss559

1-hour averages:

Reason for
il Tnitial Submittal
Change:

[Save]

A Dept. of Enviranmantal Protection DEP Home | CEM Home | Contacts | Help | Logout]

For assistance, please call DEP at (717) 7053768
between the hours of £:00 AM to 430 PM or send an e-mail to
ep-efactshelpdeskteam@state. pa.us.





	Field Label/Link
	Activity

	View Notes
	Clicking the View Notes link opens the View Notes page, which allows you to view all notes associated with this item.

Note:  This link is active only in the online CEMDPS application.  

	Add Note
	Clicking the Add Note link opens the Add Note page, which allows you to enter a note for this item.

Note:  This link is active only in the online CEMDPS application.  

	Effective Date
	Enter the effective date of the information in mm/dd/yyyy format or click the calendar icon to select a date from a calendar.  (See Date Selection for information on using the calendar to choose a date.)

	Time without Corrective Maintenance
	Enter the Manufacturer’s Claimed Time Without Corrective Maintenance in hours.

	Opacity Relative Accuracy, 1-minute averages
	Enter the Claimed Opacity Relative Accuracy, 1-minute Averages, in integer %.

	Opacity Relative Accuracy, average of 15 1-minute averages
	Enter the Claimed Opacity Relative Accuracy, Average of 15 1-minute Averages, in % in F3.1 format.

	DAS System Accuracy, 1-minute averages
	Enter the Manufacturer’s Claimed DAS System Accuracy, 1-minute Averages, in % Opacity in F6.2 format. 

	DAS System Accuracy, 1-hour averages
	Enter the Manufacturer’s Claimed DAS System Accuracy, 1-hour Averages, in % Opacity in F6.2 format.

	Reason for Information Change
	Enter a reason for information change up to 50 characters. Before you submit the monitoring plan for the first time, the default text in this text box is Initial Submittal and it is not editable.  


	Button
	Description

	Save
	Clicking Save saves the information and returns you to the Monitoring Plan page. 

	Cancel
	Clicking Cancel returns you to the Monitoring Plan page without saving changes.


 XE "Time Without Corrective Maintenance " \* MERGEFORMAT 

 XE "Relative Accuracy vs. reference method " \* MERGEFORMAT 

 XE "Relative Accuracy vs. emission standard " \* MERGEFORMAT 

 XE "Relative Accuracy in Units of Measurement " \* MERGEFORMAT 

 XE "Reason for Information Change " \* MERGEFORMAT 

 XE "Effective Date " \* MERGEFORMAT 

 XE "EDR 835 " \* MERGEFORMAT 

 XE "DAS System Accuracy, 1-Hour Averages " \* MERGEFORMAT 

 XE "Create/Edit Non-Opacity CEMS Specification Information " \* MERGEFORMAT Create/Edit Non-Opacity CEMS Specification Information (EDR 835)
The Create/Edit Non-Opacity CEMS Specification Information page records information about non-opacity CEMSs.  You must enter specification information for each non-opacity CEMS at a facility.
To add or edit Non-Opacity CEMS Specification Information, follow the instructions for each field, as listed below.  
[image: image65.jpg];;Dlrﬁ ent of Environmental Protection I’
" Bureau of Air Quality

Commonwealth of Pennsylvania

- Send essage
- View AllMessages

Inbox
20061127 0000000
| From: mTuSER
To EXTUSER

| 2006.11.27 0000000

| tis i 3 ongar ubjct

Home ~~> Eit Manitoring Plan ~-> Nan-Opacty CEMS Specification nformation

Edit Non-Opacity CEMS Specification Information

DR 835

Vi Notes | Ad Note

Effective Date: 07312007 (st be manidayyy)

Note: alfollowing values shoutd be as ciaimed by the manuacturer
Tine without

G [ hours(romatsesey

Meintenance:
Reltive Accuracy

e w pemassngy

methodt
Reltive Accuracy

oo [ % e

Acourscy,tnowr [T % of owest enisson standsrd (ot 998.96)

Reason for
e Tnitial Submittal
Change:

P4 Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout]

For assistance, please call DEP at (717) 7053768
between the hours of £:00 AM to 430 PM or send an e-mail to
ep-efactshelpdeskteam@state. pa.us.





	Field Label/Link
	Activity

	View Notes
	Clicking the View Notes link opens the View Notes page, which allows you to view all notes associated with this item.

Note:  This link is active only in the online CEMDPS application.  

	Add Note
	Clicking the Add Note link opens the Add Note page, which allows you to enter a note for this item.

Note:  This link is active only in the online CEMDPS application.  

	Effective Date
	Enter the effective date of the information in mm/dd/yyyy format or click the calendar icon to select a date from a calendar.  (See Date Selection for information on using the calendar to choose a date.)

	Time without Corrective Maintenance
	Enter the manufacturer’s claimed Time Without Corrective Maintenance in hours.

	Relative Accuracy vs. reference method
	Enter the manufacturer’s claimed Relative Accuracy vs Reference Method in % in F5.1 format.

	Relative Accuracy vs. emission standard
	Enter the manufacturer’s claimed Relative Accuracy vs Emission Standard in % in F5.1 format.

	Relative Accuracy in <units>
	Enter the manufacturer’s claimed Relative Accuracy in Btu/hr in % in F13.3 format.

	DAS System Accuracy, 1-hour averages
	Enter the manufacturer’s claimed DAS System Accuracy, 1-hour Averages, in % opacity in F6.2 format. 

	Reason for Information Change
	Enter a reason for information change up to 50 characters. Before you submit the monitoring plan for the first time, the default text in this text box is Initial Submittal and it is not editable.


	Button
	Description

	Save
	Clicking Save saves the information and returns you to the Monitoring Plan page. 

	Cancel
	Clicking Cancel returns you to the Monitoring Plan page without saving changes.


Analyzers

 XE "Units of Measurement " \* MERGEFORMAT 

 XE "Serial Number " \* MERGEFORMAT 

 XE "Sample Interface Technique " \* MERGEFORMAT 

 XE "Reason for Information Change " \* MERGEFORMAT 

 XE "Parameter/Pollutant " \* MERGEFORMAT 

 XE "Opacity/Non-Opacity " \* MERGEFORMAT 

 XE "Monitoring Point Code " \* MERGEFORMAT 

 XE "Model Number " \* MERGEFORMAT 

 XE "Manufacturer " \* MERGEFORMAT 

 XE "Linearity Limit in Analyzer's Unit of Measurement " \* MERGEFORMAT 

 XE "Linearity Limit as % of Reference Value " \* MERGEFORMAT 

 XE "Full Scale Value " \* MERGEFORMAT 

 XE "Equivalent Reading at Emission Standard Level " \* MERGEFORMAT 

 XE "Effective Date " \* MERGEFORMAT 

 XE "EDR 829 " \* MERGEFORMAT 

 XE "EDR 828 " \* MERGEFORMAT 

 XE "Create/Edit Analyzer " \* MERGEFORMAT 

 XE "Basis of Measurement " \* MERGEFORMAT 

 XE "Analytical Technique " \* MERGEFORMAT Create/Edit Analyzer (EDR 828/829)
The Create/Edit Analyzer page records information about analyzers at your facility.  An analyzer represents a measurement device (or other component, data acquisition system (DAS), etc.) used to monitor an emission or operational parameter for a particular source combination.  If your facility has multiple analyzers, you must enter and save information using this page for each existing or proposed new analyzer. 

Notes:  Each analyzer must be associated with one or more CEMSs for a particular source combination.
 To add or edit an analyzer, follow the instructions for each field, as listed below.

[image: image66.jpg]nt of Environmental Protection

Bureau of Air.

Home > Ecit Monitoring Plan ~-> Ect Analyzer

Edit Analyzer
— EDR 020 KD 025
K
~Send Message View Nstes | Ac Note
~View Al Messages
‘* Tiios Effectve Date: 2282007 | [TF] (st be memisanyy)
20081127 000000 ParameterPoltant opacty 7]
ifmm INTUSER Units of Measurement. — [%% <
To: EXTUSER
[ Basis of Measuremert.  [1UA 7]
e Monioring Point Code:  [01 %
|From WUSER Manufacturer Teco
QolEee Model Number: a0
| tisis 3 nger subect
Seriel Nuroer: ootz
FullScale Velue: oo % (Formet 933939999 393)
Expivalent Reading ot
e Tk 2 i | 4 (Formt 939399393.939)

Anaytical Techrique:  [Double Pass Transmissometry
Sample terface S
Technigue: fin-situ

Linearty Linit &5

% of Reference Value:

.
g 4 Fornat s a0
OpacityNon-Opacity: Opacity b

Reasontoomomons  [oavias swmivemr B

Change:

B % (Format 999.99)

Save | [ Cancel

A Dept. of Enviranmantal Protection DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (717) 7053768
between the hours of £:00 AM to 430 PM or send an e-mailto
ep-efactshelpdeskteam@state. pa.us.





	Field Label/Link
	Activity

	View Notes
	Clicking the View Notes link opens the View Notes page, which allows you to view all notes associated with this item.

Note:  This link is active only in the online CEMDPS application.   

	Add Note
	Clicking the Add Note link opens the Add Note page, which allows you to enter a note for this item.

Note:  This link is active only in the online CEMDPS application. 

	Effective Date
	Enter the effective date of the information in mm/dd/yyyy format or click the calendar icon to select a date from a calendar.  (See Date Selection for information on using the calendar to choose a date.)

	Parameter/Pollutant


	Use the drop-down list to enter the Parameter/Pollutant for the analyzer. The drop-down list contains the valid values for this field.  If the value you need is not in the drop-down list, please contact the DEP to request that a new value be added.

Examples of acceptable values are:

CE

CO

C02

Culm Gas %

Flow

Fuel Rate

H2O

H2S

HC

HCl

HCl Reduction

Heat Input

NO

NO2

NOx

NOx Allowable

O2

Opacity

Pressure

SO2

SO2 Allowable

SO2 Reduction

Steam Flow

Temperature

TRS

VCM

VOC



	Units of Measurement
	Use the drop-down list to enter the Units of Measurement. The drop-down list contains the valid values for this field.  If the value you need is not in the drop-down list, please contact the DEP to request that a new value be added.

Examples of acceptable values are:

%

Btu/hr

cfh

Cfm

Degrees F

gph

gpm

lbs/hr

lbs/Mbtu

lbs/ton

Mbtu/hr

Mcfh

ppm

psi



	Basis of Measurement
	Use the drop-down list to enter the Basis of Measurement. The drop-down list contains the valid values for this field.  If the value you need is not in the drop-down list, please contact the DEP to request that a new value be added.

Examples of acceptable values are:

· Wet

· Dry

· N/A

	Monitoring Point Code
	Use the drop-down list to enter the Monitoring Point Code. The drop-down list contains the valid values for this field.  If the value you need is not in the drop-down list, please contact the DEP to request that a new value be added.

Examples of acceptable values are:

· For outlet, use letter O followed by numeral to uniquely identify analyzer

· For inlet, use letter I followed by numeral to uniquely identify analyzer

· For Primary Temperature, use letter P followed by numeral to uniquely identify analyzer

· For Secondary Temperature, use letter S followed by numeral to uniquely identify analyzer

	Manufacturer
	Enter the Manufacturer Name for the analyzer.

	Model Number
	Enter the Model Number for the analyzer.

	Serial Number
	Enter the Serial Number for the analyzer.  If the actual analyzer has not yet been received, leave this field blank and upon reception of the analyzer, submit a record type 829 with the Reason For Information Change Flag set to R in order to correct the Serial Number information.

	Full Scale Value
	Enter the Full Scale Value for the analyzer in units of analyzer measurement in the format F13.3.  

	Equivalent Reading at Emission Standard Level
	Enter the Equivalent Reading at Emission Level for the analyzer at the lowest applicable emission standard in the format F13.3.  Determination of this value is explained in the Continuous Source Monitoring Manual.  

	Analytical Technique
	Use the drop-down list to enter the Analytical Technique. The drop-down list contains the valid values for this field.  If the value you need is not in the drop-down list, please contact the DEP to request that a new value be added.

Examples of acceptable values are:

2nd Derivative UV

Chemiluminescence

Coulometric Titration

Differential Pressure

Diffusion/absorption

Double Pass Transmissometry

Electrochemical Cell

Fluorescence 

Fuel Cell

Fuel Sampling

GC 

Ion Mobility Spectrometry

IRGFC 

Lead Acetate Tape

NA

NDIR 

NDUV 

Orifice Plate

Paramagnetic 

Single Pass Transmissometry

Thermal Mass Flow

Thermocouple 

Ultrasonic 

UV Diode Array

Vortex Flowmeter

Wheel Meter



	Sample Interface Technique
	Use the drop-down list to enter the Sample Interface Technique. The drop-down list contains the valid values for this field.  If the value you need is not in the drop-down list, please contact the DEP to request that a new value be added.

Examples of acceptable values are:

· Extractive

· Dilution Extractive

· In-situ

· Dilution In-situ

· Not Applicable

	Linearity Limit as % of Reference Value
	Enter the Linearity Limit as % of Reference Value for the analyzer in F6.2 format.

	Linearity Limit in Analyzer's Unit of Measurement
	Enter the Linearity Limit in Units of Measurement for the analyzer in F13.3 format. 

	Opacity/Non-Opacity
	Use the drop-down list to enter whether the analyzer is Opacity or Non-Opacity.

	Reason for Information Change
	Enter a reason for information change up to 50 characters. Before you submit the monitoring plan for the first time, the default text in this text box is Initial Submittal and it is not editable.  


	Button
	Description

	Save
	Clicking Save saves the information and returns you to the Monitoring Plan page. 

	Cancel
	Clicking Cancel returns you to the Monitoring Plan page without saving changes.


 XE "Reason for Information Change " \* MERGEFORMAT 

 XE "Manufacturer's claimed linearity as unit of measurement " \* MERGEFORMAT 

 XE "Manufacturer's claimed linearity as % of reference value " \* MERGEFORMAT 

 XE "Manufacturer's claimed cycle time in seconds " \* MERGEFORMAT 

 XE "Manufacturer's claimed 7-day calibration error as unit of measurement " \* MERGEFORMAT 

 XE "Manufacturer's claimed 7-day calibration error as % of reference value " \* MERGEFORMAT 

 XE "Manufacturer's claimed 7-day calibration error as % of equivalent ... " \* MERGEFORMAT 

 XE "Effective Date " \* MERGEFORMAT 

 XE "EDR 840 " \* MERGEFORMAT 

 XE "Create/Edit Analyzer Opacity and Non-Opacity Specification Information " \* MERGEFORMAT Create/Edit Analyzer Opacity and Non-Opacity Specification Information (EDR 840)

The Create/Edit Analyzer Opacity and Non-Opacity Specification Information page records manufacturer's claimed linearity, 7-day calibration, and cycle time for both opacity and non-opacity analyzers.  You must enter this specification information for every analyzer at a facility.

To add or edit Analyzer Opacity and Non-Opacity Specification Information, follow the instructions for each field, as listed below.  

[image: image67.jpg]CEMDPS

Commonwealth of Pennsylvani
nt of Environmental Protection
Bureau of Air Quality

- Send Message
- View AllMessages

!
——

| 2006-11-27 om0m008

| From: INTUSER
1o iU
o
| 2008-11-27 00:00:00.0
[
|1 EXTUSER

| s 3onger subject

Home ~~> Edit Monitring Plan ~~> Analyzer Opacty and Non-Opacy Specifcation information

Analyzer Opacity and Non-Opacity Specification Informat

EDR 040

View Notes | Ad Note

Effective Date: 02282007 | st v maniaayyyy)
Menutacturer's
clamed inearity as 3 (Formet 393.39)

% of reference value:
Menutacturer's

clamed ineartty as 3 (Formet 393939939 939)

unit of measuremert:

Menutacturer's
Climed 7-day

calbratonerroras 2 (Formet 393.39)
% of equivalert value

o emission standarc:

Menutacturer's

chined7-day
colbrationerroras 2| (Format 933.39)

% of reference value:

Menutacturer's
Climed 7-day
calkration emor as
unit of measuremert:

(Format 399939939 939)

Menutacturer's
clained cycke tine in | Format sess)

seconds

Reason for T a— |
Information frivial Submical

Change:

[save ]| [Cancet |

P4 Dept. of Emvironmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (717) 705.3768
between the hours of £:00 AM to 4:30 PM or send an e-mailto
ep-efactshelpdeskteam@state. pa.us.





	Field Label/Link
	Activity

	View Notes
	Clicking the View Notes link opens the View Notes page, which allows you to view all notes associated with this item.

Note:  This link is active only in the online CEMDPS application.  

	Add Note
	Clicking the Add Note link opens the Add Note page, which allows you to enter a note for this item.

Note:  This link is active only in the online CEMDPS application.  

	Effective Date
	Enter the effective date of the information in mm/dd/yyyy format or click the calendar icon to select a date from a calendar.  (See Date Selection for information on using the calendar to choose a date.)

	Manufacturer's claimed linearity as % of reference value
	Report the Manufacturer’s Claimed Linearity as % of Reference Value in F6.2 format. 

	Manufacturer's claimed linearity as unit of measurement
	Report the Manufacturer’s Claimed Linearity as Units of Measurement in F13.3 format.

	Manufacturer's claimed 7-day calibration error as % of equivalent value at emission standard
	Report the Manufacturer’s Claimed 7-day Calibration Error as % of Equivalent Value at Emission Standard in F6.2 format.

	Manufacturer's claimed 7-day calibration error as % of reference value
	Report the Manufacturer’s Claimed 7-day Calibration Error as % of Reference Value in F6.2 format.

	Manufacturer's claimed 7-day calibration error as unit of measurement
	Report the Manufacturer’s Claimed 7-day Calibration Error as Units of Measurement in F13.3 format.

	Manufacturer's claimed cycle time in seconds
	Report the Manufacturer’s Claimed Cycle Time in I4 format. 

	Reason for Information Change
	Enter a reason for information change up to 50 characters. Before you submit the monitoring plan for the first time, the default text in this text box is Initial Submittal and it is not editable. 


	Button
	Description

	Save
	Clicking Save saves the information and returns you to the Monitoring Plan page. 

	Cancel
	Clicking Cancel returns you to the Monitoring Plan page without saving changes.


 XE "Reason for Information Change " \* MERGEFORMAT 

 XE "Number of Zero and Calibration Checks per Week " \* MERGEFORMAT 

 XE "Monitor Pathlength " \* MERGEFORMAT 

 XE "Expected Normal Reading " \* MERGEFORMAT 

 XE "Expected Maximum Reading " \* MERGEFORMAT 

 XE "Emission Outlet Pathlength " \* MERGEFORMAT 

 XE "Effective Date " \* MERGEFORMAT 

 XE "EDR 837 " \* MERGEFORMAT 

 XE "Data Recorder Resolution in Seconds " \* MERGEFORMAT 

 XE "Data Recorder Resolution in Analyzer's Unit of Measurement " \* MERGEFORMAT 

 XE "Data Recorder Resolution in % of Equivalent Reading at Emission Level " \* MERGEFORMAT 

 XE "Cycles Per Hour, Record " \* MERGEFORMAT 

 XE "Cycles Per Hour, Measure " \* MERGEFORMAT 

 XE "Create/Edit Opacity Analyzer Specification Information " \* MERGEFORMAT 

 XE "Certificate of Conformance with ASTM D6216-03 has been obtained " \* MERGEFORMAT Create/Edit Opacity Analyzer Specification Information (EDR 837)
The Create/Edit Opacity Analyzer Specification Information page records information about opacity analyzers.  You must enter specification information for each opacity analyzer at a facility.
To add or edit Opacity Analyzer Specification Information, follow the instructions for each field, as listed below.  When finished, click Save at the bottom of the page.  

[image: image68.jpg]CEMDPS I i,

Bureau of Air Quality

{— \
| From: INTUSER

| 2005-11-27 000000

From mTUsER
To: EXTUSER

| s 3onger subject

Horme - Eit Moritoring Plan ~~> Opacty Anslyzer Specification nformation

Edit Opacity Analyzer Specification Information
R 037

View Notes | Ad Note

Effective Date: 02282007 = st o memiaayyy)
Expected Normal

ey b % (Format 939999393.398)
Expectediiminn 55—

Reading o 96(Format 339393999.999)
Certficate of

Conformance e
wih ASTM De215-03 | Yo%

has been abtained:

Monitor Patriengtr (502 Feet (Fornat 39.36)
Emission Outlet oo
Pathiength: (23081 | Feet (Format 03.59)

Deta Resorder Resolution
- % of Exuivalent

= —
A — T
-
e
of Measuremert: il (Format 999939939.939)
- s s Je—
sttt a— T
o e

Record
Number of Zera and
Calibration | Format agg)
Creckeperwee

Reason for [aicial sEtecar B
Information fricial submictal

Change:

[save ]| [Cancet |

P4 Dept. of Emvironmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (717) 705.3768
between the hours of £:00 AM to 4:30 PM or send an e-mailto
ep-efactshelpdeskteam@state. pa.us.





	Field Label/Link
	Activity

	View Notes
	Clicking the View Notes link opens the View Notes page, which allows you to view all notes associated with this item.

Note:  This link is active only in the online CEMDPS application.  

	Add Note
	Clicking the Add Note link opens the Add Note page, which allows you to enter a note for this item.

Note:  This link is active only in the online CEMDPS application.  

	Effective Date
	Enter the effective date of the information in mm/dd/yyyy format or click the calendar icon to select a date from a calendar.  (See Date Selection for information on using the calendar to choose a date.)

	Expected Normal Reading
	Enter the Expected Normal Reading for the analyzer in the analyzer's units of measurement in F13.3 format.  

	Expected Maximum Reading
	Enter the Expected Maximum Reading for the analyzer in the analyzer's units of measurement in F13.3 format.

	Certificate of Conformance with ASTM D6216-03 has been obtained
	Use the drop-down list to answer Yes or No.

	Monitor Pathlength
	Enter the Monitor Pathlength in feet in F5.2 format.

	Emission Outlet Pathlength
	Enter the Emission Outlet Pathlength in feet in F6.2 format.

	Data Recorder Resolution in:
	

	 % of Equivalent Reading at Emission Limit
	Enter the Data Recorder Resolution in % of Equivalent Reading at Emission Limit in F6.2 format. 

	Analyzer's Unit of Measurement
	Enter the Data Recorder Resolution in Unit of Measurement in F13.3 format.



	Seconds
	Enter the Data Recorder Resolution in Seconds in I4 format.

	Number of Cycles Per Hour, Measure
	Enter the Number of Cycles per Hour, Measure in I3 format.

	Number of Cycles Per Hour, Record
	Enter the Number of Cycles per Hour, Record in I3 format.

	Number of Zero and Calibration Checks per Week
	Enter the Number of Zero and Calibration Checks per Week in I3 Format.

	Reason for Information Change
	Enter a reason for information change up to 50 characters. Before you submit the monitoring plan for the first time, the default text in this text box is Initial Submittal and it is not editable. 


	Button
	Description

	Save
	Clicking Save saves the information and returns you to the Monitoring Plan page. 

	Cancel
	Clicking Cancel returns you to the Monitoring Plan page without saving changes.


 XE "Reason for Information Change " \* MERGEFORMAT 

 XE "Number of Zero and Calibration Checks per Week " \* MERGEFORMAT 

 XE "Number of Cycles Per Hour, Measure and Record " \* MERGEFORMAT 

 XE "Expected Normal Reading " \* MERGEFORMAT 

 XE "Expected Maximum Reading " \* MERGEFORMAT 

 XE "Effective Date " \* MERGEFORMAT 

 XE "EDR 836 " \* MERGEFORMAT 

 XE "Data Recorder Resolution in Seconds " \* MERGEFORMAT 

 XE "Data Recorder Resolution in Analyzer's Unit of Measurement " \* MERGEFORMAT 

 XE "Data Recorder Resolution in % of Equivalent Reading at Emission Level " \* MERGEFORMAT 

 XE "Create/Edit Non-Opacity Analyzer Specification Information " \* MERGEFORMAT Create/Edit Non-Opacity Analyzer Specification Information (EDR 836)
The Create/Edit Non-Opacity Analyzer Specification Information records information about non-opacity analyzers.  You must enter specification information for each non-opacity analyzer at a facility.
To add or edit Non-Opacity Analyzer Specification Information, follow the instructions for each field, as listed below. 

[image: image69.jpg]c h of P
EMDPSIE o et

Bureau of Air Quality

Home -~ Ecit Moritoring Plan ~~> Non-Opacly Analyzer Specification information

Edit Non-Opacity Analyzer Specification Information

‘ [ mbex

| 2008-11-27 000000
| From: INTUSER

7o extusex

en

| 2008-11-27 000000
From: INTUSER.

To: EXTUSER

i 5 3 longersubject

—_— e 836
[ Ccorespondence

~Send Message

View Al Messages Effective Date: [ B onustve mmisasyyyy

Eecedtomal [
Restits % (Format 939999393.398)

R |
Reading 95(Format 399393099 999)

Deta Recorder Resoluton
- 9% of Equivalent

Reo [ —T T

ot Emission Lini:

- srdyzers Uniof [
Measrare (Formet 293929939.939)

secons [ omatsen

b of Cyses Per
i [ —T
s et e

Number of Zero and

Cameon [ —T

Checks per Week:

Reason for
A Tnitial Submittal
Change:

[save]

P4 Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (717) 705-3768
between the hours of £:00 AM to 430 PM or send an e-mail to
ep-efactshelpdeskteam@state. pa.us.





	Field Label/Link
	Activity

	View Notes
	Clicking the View Notes link opens the View Notes page, which allows you to view all notes associated with this item.

Note:  This link is active only in the online CEMDPS application.  

	Add Note
	Clicking the Add Note link opens the Add Note page, which allows you to enter a note for this item.

Note:  This link is active only in the online CEMDPS application.  

	Effective Date
	Enter the effective date of the information in mm/dd/yyyy format or click the calendar icon to select a date from a calendar.  (See Date Selection for information on using the calendar to choose a date.)

	Expected Normal Reading
	Enter the Expected Normal Reading for the analyzer in units of measurement in F13.3 format. 

	Expected Maximum Reading
	Enter the Expected Maximum Reading for the analyzer in units of measurement in F13.3 format. 

	Data Recorder Resolution in:
	

	% of Equivalent Reading at Emission Limit
	Enter the Data Recorder Resolution in % of Equivalent Reading at Emission Limit in F6.2 format. 

	Analyzer's Unit of Measurement
	Enter the Data Recorder Resolution in Unit of Measurement in F13.3 format.

	Seconds
	Enter the Data Recorder Resolution in Seconds in I4 format.

	Number of Cycles Per Hour, Measure and Record
	Enter the Number of Cycles Per Hour, Measure and Record in I3 format.

	Number of Zero and Calibration Checks per Week
	Enter the Number of Zero and Calibration Checks per Week in I3 format.

	Reason for Information Change
	Enter a reason for information change up to 50 characters. Before you submit the monitoring plan for the first time, the default text in this text box is Initial Submittal and it is not editable. 


	Button
	Description

	Save
	Clicking Save saves the information and returns you to the Monitoring Plan page. 

	Cancel
	Clicking Cancel returns you to the Monitoring Plan page without saving changes.


 XE "EDR 830 " \* MERGEFORMAT 

 XE "Calibration Error Limit Config " \* MERGEFORMAT 

 XE "And/Or Code " \* MERGEFORMAT Calibration Error Limit (EDR 830)

The Calibration Error Limits page displays a list of calibration error limits already configured for an analyzer.  The page title includes the name of the analyzer associated with the calibration error limits listed.  For example, when you view the calibration error limits for an analyzer called "Opacity %," the page title is Calibration Error Limit for Opacity %.  From the Calibration Error Limit page, you can add a calibration error limit for the analyzer or edit or remove an existing limit.

The table below describes the information displayed in the Calibration Error Limit page and the options available. 

[image: image70.jpg]~ Commonwealth of Pennsylvania "
EMDPS ent of Environmental Protection
Bureau of Air Quality

Home ~-> it Manitoing Plan ~-> Ect Calloration Error Liits

ration Error Limit for
Opacity %

e
[ Correspondence EDR 830

- Send Message
SVt AlEses Calibration Error Limit Config AndOr Code

N | rreerer ~
FrrETe —

 From: NTUSER
o xTusER
et

Ccal

| 2008-11-27 000000
From: INTUSER.

To: EXTUSER

| s 3 onger subjet

A Dept. of Enviranmantal Protection DEP Home | CEM Home | Contacts | Help | Logout]
For assistance, please call DEP at (T17) 7053768
between the hours of £:00 AM to 430 PM or send an e-mailto
ep-efactshelpdeskteam@state.pa.us.





	Column
	Description

	Calibration Error Limit Config
	Displays a list of calibration error limits configured for an analyzer

	And/Or Code
	Displays the And/Or designation for the error limit


	Button
	Description

	Add
	Click Add to enter a new calibration error limit. The Create/Edit Calibration Error Limit page displays.

	Edit
	Click Edit next to the appropriate error limit to make changes to that limit.  The Create/Edit Calibration Error Limit page displays.

	Remove
	Click Remove next to the appropriate error limit to remove it from the error limits list. Clicking this link opens the Delete <Item> page, which allows you to confirm or cancel the deletion.


 XE "Reason for Information Change " \* MERGEFORMAT 

 XE "Effective Date " \* MERGEFORMAT 

 XE "EDR 830 " \* MERGEFORMAT 

 XE "Create/Edit Calibration Error Limit " \* MERGEFORMAT 

 XE "Calibration Error Limit Value - Units of Measurmt " \* MERGEFORMAT 

 XE "Calibration Error Limit Value - % of Refer. Value " \* MERGEFORMAT 

 XE "Calibration Error Limit Value - % of Equiv. Value " \* MERGEFORMAT 

 XE "Calibration Error Limit ID Code " \* MERGEFORMAT 

 XE "And/Or Standard (for or'd Standards) " \* MERGEFORMAT Create/Edit Calibration Error Limit (EDR 830)
The Create/Edit Calibration Error Limit page records information about calibration error limits for analyzers.  You must enter at least one calibration error limit for each analyzer at a facility.
To add or edit a Calibration Error Limit, follow the instructions for each field, as listed below.  
[image: image71.jpg]CEMDPS

Commonwealth of Pennsylvania
nt of Environmental Protection
Bureau of Air

Correspondence

- Send Message
- View AllMessages

2008-11-27 00:00:000
From: NTUSER
To: EXTUSER

2008-11-27 00:00:000
From: INTUSER.

To: EXTUSER

Home ~~> it Manitoring Plan ~-> EdtCaliraton Ertor Limt

Edit Calibration Error Limit

DR 030

View Notes | Ad Note

Effective Date: o7m1z007

| st v maniaayyyy)

Cabration Evor Ut [t
ot 2ahour brift

Calbration Error Liit

Value - % of Equiv. 1

Format 839.89

Value:
Calbration Error Lt

Value - % of Refer. 1

Format 389.89

Value:
Calbration Error Liit

Value-Untsof 3

Format 399393999 989939

Measurmt,

Anor Stverd (o [
orastandarssy 14"

Reason for Tnitial submictal

Infarmation
Change:

Swve] [Ganoet |

P4 Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (717) 7053768
between the hours of £:00 AM to 430 PM or send an e-mail to
ep-efactshelpdeskteam@state. pa.us.





	Field Label/Link
	Activity

	View Notes
	Clicking the View Notes link opens the View Notes page, which allows you to view all notes associated with this item.

Note:  This link is active only in the online CEMDPS application.  

	Add Note
	Clicking the Add Note link opens the Add Note page, which allows you to enter a note for this item.

Note:  This link is active only in the online CEMDPS application.  

	Effective Date
	Enter the effective date of the information in mm/dd/yyyy format or click the calendar icon to select a date from a calendar.  (See Date Selection for information on using the calendar to choose a date.)

	Calibration Error Limit ID Code
	Use the drop-down list to enter the Calibration Error Limit ID Code. The drop-down list contains the valid values for this field.  If the value you need is not in the drop-down list, please contact the DEP to request that a new value be added.

Examples of acceptable values are:

· 2-hour (2)

· 24-hour (24)

	Calibration Error Limit Value - % of Equiv. Value
	Enter the Calibration Error Limit Value  - % of Equiv. Value (as specified in the Continuous Source Monitoring Manual) in the format F6.2.  

	Calibration Error Limit Value - % of Refer. Value
	Enter the Calibration Error Limit Value - % of Refer. Value (as specified in the Continuous Source Monitoring Manual) in the format F6.2.

	Calibration Error Limit Value -  Units of Measurmt
	Enter the Calibration Error Limit Value - Units of Measurement (as specified in the Continuous Source Monitoring Manual) in the format F6.2.  

	And/Or Standard (for or'd Standards)
	Use the drop-down list to enter And, since currently all calibration error standards are "And'd".

	Reason for Information Change
	Enter a reason for information change up to 50 characters. Before you submit the monitoring plan for the first time, the default text in this text box is Initial Submittal and it is not editable.  


	Button
	Description

	Save
	Clicking Save saves the information and returns you to the Calibration Error Limit page. 

	Cancel
	Clicking Cancel returns you to the Calibration Error Limit page without saving changes.


Test Protocols

 XE "Validate Submittal " \* MERGEFORMAT Test Protocol

The Test Protocol page displays the proposed test date, testing firm, analytical labs, and CEMSs to be tested for a particular test protocol.  The page title includes the test protocol ID.  

From this page you can add or adjust the test date and add or edit the test firm, analytical labs, and CEMSs to be tested.  Using the expand (+) and collapse (-) symbols, you can display or hide information as follows:

· Click the plus sign (+) in front of any heading to view more detailed information about that heading or to access more options.  Information and available options display indented beneath the heading expanded.

· Click the minus sign (-) in front of any heading to collapse (hide) the details displayed beneath it.

· Click the Expand All link to display all information and options beneath all headings at once.

· Click the Collapse All link to collapse the entire hierarchy of information, hiding all details except for the main headings.

The following sections describe the options available on the Test Protocol page.

[image: image72.jpg]~ Commonwealth of Pennsylvania
ent of Environmental Protection I
Bureau of Air Quality

Home ~-> Eit Test Protacel

Test Protocol #174
[ Conespondonce
- Send Message. Basic Information
-View Al Messages Primary Facity i 510331

‘ Inbox Conpany Neme:  CASTLE RUBBER LLC.

| 2008-11-27 0000000
ime INTUSER

FaciyName:  CASTLE RUBBER LLCEEAST BUTLER BORO

o EXTUSER Status: Initsted

Remove Test Protocol

To: EXTUSER View al llotes for this Test Protocol

[sisabmgerstes |

Expand Al Collapse Al

Proposed Test Date: oasr2007

Test Firm eor sos eor soa

Test Purpose: ntial Cetication of CEMS

Testing Protocol Attachment: EDRBDS x

Contact ion = Juor s0a mom s0s
[

Frsthame Alexander

Vi st

Lasthame: Bell

Tt CEopresident

Adress Line 1: 101 llorth Second St.
Adress Line 2

cy: Reading

ssylvania
ZpCode  AT013-1234

State: Pen

Phone Number. 77 - 243 - 4367

FaxNuer

E-ml Acress: abellverizonaet

@ Analytical Laboratories (2) gr sos zmx 806
Clck the 3 buton to expand

@ CEMS to be Tested (2) mx 807
Clck the B buton to expand

PA Dagt, of Environmental Prtaction DEP Home | CEM Home | Contacts | Help | Logout]
For assistance, please call DEP at (717) 7053768
between the hours of £:00 AM to 4:30 PM or send an e-mail to
ep-efactshelpdeskteam@state. pa.us.





Basic Information

The Basic Information section displays four pieces of information associated with the test protocol as follows:

	Field Label
	Description

	Primary Facility Id
	Displays the facility ID for which the test protocol is being submitted.

	Company
	Displays the name of the company associated with the test protocol.

	Facility
	Displays the name of the facility associated with the test protocol.

	Status
	Displays the status of the test protocol as follows:

Status

Description

Initiated

A test protocol is considered Initiated if you have begun entering data for your test protocol but have not yet submitted the information for DEP review.  Only facility users may work with the submittal package while it has this status.

Submitted

A test protocol is considered Submitted if you have submitted your test protocol information for DEP review.  Only DEP reviewers and approvers may work with the submitted data when the test protocol has this status.  You will be able to view the information, but not change it.

Submitted (Partial Submittal)

This status is similar to the Submitted status, but is used to identify a partial submittal.  Partial Submittals normally occur with quarterly reports.  

Review

Once you submit your test protocol, the status changes to Review as DEP reviewers examine your submittal.

Revision

If DEP reviewers find issues with a submittal, they may reject it and request that data be changed or verified by the facility.  In this instance, the test protocol is given the status of Revision, and you may revise the information and resubmit the plan.  Only facility users may work with the test protocol information while it has this status.

Review Complete

After reviewers evaluate and render a decision on the test protocol submission, they move the test protocol into Review Complete status.  At this point, the submission is waiting for a DEP approver to login and verify the reviewer's decision.  No one can change the test protocol submission through the CEMDPS application while it has this status.  Approvers automatically receive an email notification indicating that a reviewed submission is awaiting their approval.

Approved

This is the final status of a submission.  This status indicates that an approver approved the decision made by a reviewer.  When the submission enters Approved status, you, and other defined users at your facility, automatically receive an email notification from the CEMDPS.  No one may change the test protocol data through the CEMDPS once it reaches this status.  Facility users and DEP approvers and reviewers may still view the test protocol information through the PDF file.

Hold

A reviewer or approver may place the test protocol submission in Hold status.  The Hold status remains until the submission is reassigned.



	Submitted By
	Displays the name of the person who submitted the test protocol.


	Button
	Description

	Add
	The Add button displays when no submitter information is specified.  Click Add to enter submitter information for the test protocol.  The Create Submitter Information  page displays.

	Edit
	The Edit button displays when submitter information is already specified. Click Edit to edit submitter information for the test protocol.  The Edit Submitter Information  page displays.


The Remove Test Protocol Link

The Remove Test Protocol link lets you delete the test protocol.  Clicking this link opens the Delete <Item> page, which allows you to confirm or cancel the deletion.

The View all Notes for this Test Protocol Link

The View all Notes for this Test Protocol link opens the View Notes page and allows you to view all notes associated with the components of the test protocol.  

Note:  The View all Notes for this Test Protocol link is available only in the online CEMDPS application.  

Proposed Test Date

This area displays the proposed test date entered for the test protocol.  To edit the proposed test date, click Edit to access the Set Proposed Testing Date page.

Test Firm

This area displays the test firm associated with the test protocol and includes the test purpose, the test protocol attachment, and contact information for the test firm.  The EDR numbers associated with configuring test firms display for your convenience.

Options available for configuring test firms appear in the table below.

	Button
	Description

	Edit
	Click Edit next to the test firm to make changes to that firm. The Create/Edit Testing Firm page displays.

	Remove
	Click Remove next to the test firm to remove that firm from the test protocol. Clicking this link opens the Delete <Item> page, which allows you to confirm or cancel the deletion.


Analytical Laboratories

The Analytical Laboratories heading appears underneath the test firm.  The number of laboratories associated with the test firm appears in parentheses next to the heading.  When you expand (+) the Analytical Laboratories heading, each lab's name displays highlighted in purple with the lab's contact information underneath. The EDR numbers associated with configuring analytical laboratories display for your convenience.

[image: image73.jpg]© Analytical Laboratories (2) L2/ |gpr g05 zom so¢

EbR s0s IR 806

P Environmental Leb
Aceredidation Act 123456
Registration Number:

Salutation: .
FrstName: Jobn

Mkl il 3

Last Narme: Roberts

Tt Manager
AdiressLinet: 13976 Sterling Bivd
AdiressLne2  Sute 342

cty. Camp Hin

Stae Pennsyivania

Zn ot 10115555

Phone fumber. 147585 - 1212
Fax b 75551212

EnslAddress:  Jroberts@yaoem.com




Options available for configuring analytical laboratories appear in the table below.

	Button
	Description

	Add
	Click Add to enter a new analytical laboratory. The Create/Edit Analytical Laboratory page displays.

	Edit
	Click Edit next to the appropriate analytical laboratory to make changes to that lab. The Create/Edit Analytical Laboratory page displays.

	Remove
	Click Remove next to the appropriate analytical laboratory to remove that laboratory from the test firm.


CEMS to be Tested

The CEMS to be Tested heading also appears underneath each test firm. The number of CEMS to be tested associated with a test firm appears in parentheses next to the heading.  When you expand (+) the CEMS to be Tested heading, a table listing each CEMS to be tested displays underneath, and the EDR number associated with configuring CEMS to be tested displays for your convenience.

[image: image74.jpg]£ CEMS to be Tested (2) o8 807
Sowrce
cemsp  Source Emission Result Tvwe Staws
15208 12 o< stEt PRMARY  Approved

15208 unit 13 Opacty % PRMARY  Pending Phase 3





To add or edit CEMS to be tested, click Edit to access the Create/Edit CEMS to Be Tested page.  Information that displays about CEMS to be tested is described in the table below.

	Column
	Description

	CEMSID
	Displays the CEMS ID for the CEMSs defined for the source combination and emission result listed.

	Source Combination
	Displays the source combination name.

	Emission Result
	Displays the emission result associated with the source combination listed.

	Type
	Indicates whether the CEMS is the Primary CEMS, a Backup, or a Standby.

	Status
	Indicates the current status of the CEMS.


The Validate Submittal Button

The DEP requires test protocol data fields to be submitted in specific formats, which are indicated where applicable in CEMDPS pages, and to follow business rules outlined in the current Continuous Source Monitoring Manual (CSMM).  At the top of the Test Protocol page, click Validate Submittal to have the CEMDPS check the data you entered to ensure it's in the proper format and follows CSMM business rules before you submit the protocol.  After the validation process, the Test Protocol Submittal page displays. This page either confirms that all data was validated or lists errors that must be addressed before submitting the protocol.  Please see Test Protocol Submittal Page for more information.

 XE "Zip Code " \* MERGEFORMAT 

 XE "Title " \* MERGEFORMAT 

 XE "State " \* MERGEFORMAT 

 XE "Salutation " \* MERGEFORMAT 

 XE "Phone Number " \* MERGEFORMAT 

 XE "Middle Initial " \* MERGEFORMAT 

 XE "Last Name " \* MERGEFORMAT 

 XE "First Name " \* MERGEFORMAT 

 XE "Fax Number " \* MERGEFORMAT 

 XE "EDR 802 " \* MERGEFORMAT 

 XE "EDR 801 " \* MERGEFORMAT 

 XE "E-mail Address " \* MERGEFORMAT 

 XE "Create/Edit Submitter Information " \* MERGEFORMAT 

 XE "Company Name " \* MERGEFORMAT 

 XE "Comments " \* MERGEFORMAT 

 XE "City " \* MERGEFORMAT 

 XE "Address Line 2 " \* MERGEFORMAT 

 XE "Address Line 1 " \* MERGEFORMAT Create/Edit Submitter Information (EDR 801/802)

The Create/Edit Submitter Information page records information concerning the submitter of the data.  

To add or edit submitter information, follow the instructions for each field, as listed below.  

[image: image75.jpg]Commonvealth of Pennsylvania =
ent of Environmental Protection I’
g Bureau of Air Quality

Home > Montoring Plan Ecit Page -~ Submiter Information

Edit Submitter Information
EDR 001 EDR 802

“Send essage View Notes | Ad Note

- View AllMessages

Submitter Informati

2008-11-27 00:00:000 Conpy lare.

 From: NTUSER Sabtation
[HEEE Frsthame:  [lim
= Wil o

2008-11-27 00:00:000
From: INTUSER.
To BXTUSER Til:

his 5 3 ongersubject

Last Name:

Address Line 1

Address Line 2

ciy

g

Fax Number:

Email acdress: [ckuchars@state.pa.
Commerts:  [mp upload from MP279

] -] -]
] -] -]

A Dept. of Enviranmantal Protection DEP Home | CEM Home | Contacts | Help | Logout]

For assistance, please call DEP at (717) 7053768
between the hours of £:00 AM to 430 PM or send an e-mailto
ep-efactshelpdeskteam@state. pa.us.





	Field Label
	Activity

	Company Name
	Enter the company name of the person submitting the EDR.

	Salutation
	Enter the preferred correspondence salutation for the person submitting the EDR.

	First Name
	Enter the first name of the person submitting the EDR.

	Middle Initial
	Enter the middle initial of the person submitting the EDR.  If the person has no middle initial, leave this field blank.

	Last Name
	Enter the last name of the person submitting the EDR.

	Title
	Enter the title of the person submitting the EDR.

	Address Line 1
	Enter the first line of the street address of the person submitting the EDR.

	Address Line 2
	Enter the second line of the street address of the person submitting the EDR.  If there is no second line of the street address, leave this field blank.

	City
	Enter the city name of the person submitting the EDR.

	State
	Use the drop-down list to enter the state postal code of the person submitting the EDR.

	Zip Code
	Enter the 5-digit zip code and the 4-digit zip plus 4 code of the person submitting the EDR.

	Phone Number
	Enter the 10-digit phone number of the person submitting the EDR.

	Fax Number
	Enter the 10-digit fax number of the person submitting the EDR.  If the person submitting the EDR has no fax, leave this field blank.

	E-mail Address
	Enter the e-mail address of the person submitting the EDR.  If the person submitting the EDR has no e-mail address, leave this field blank.


	Button
	Description

	Save
	Clicking Save saves the contact information and returns you to the previous page.

	Cancel
	Clicking Cancel returns you to the previous  page without saving changes.


 XE "Set Proposed Testing Date " \* MERGEFORMAT 

 XE "Proposed Testing Date " \* MERGEFORMAT 

 XE "EDR 803 " \* MERGEFORMAT Set Proposed Testing Date (EDR 803)

The Set Proposed Testing Date page allows you to enter the date on which you plan to run a test at your facility.  

To set a proposed testing date, enter the date in mm/dd/yyyy format or click the calendar icon to select a date from a calendar.  (See Date Selection for information on using the calendar to choose a date.) Click Save when finished.

[image: image76.jpg]r}ommnnweann}mmymm-
ent of Environmental Protection P

Bureau of Air Quality

Home ~> Edit Test Protacel --> Set Proposed Testing Date

Set Proposed Testing Date

—_— DR 003
Correspondence

- Send Message

e Proposed Testing
Visw Al Mssage e 03302007
2008-11-27 00:00:000 =
 From: NTUSER
To: EXTUSER
2008-11-27 00:00:000
From: INTUSER.
To: EXTUSER

his 5 3 ongersubject

(st be maniddyyyy)

A Dept. of Enviranmantal Protection DEP Home | CEM Home | Contacts | Help | Logout]
For assistance, please call DEP at (T17) 7053768
between the hours of £:00 AM to 430 PM or send an e-mailto
ep-efactshelpdeskteam@state.pa.us.





 XE "Zip Code " \* MERGEFORMAT 

 XE "Title " \* MERGEFORMAT 

 XE "Test Purpose " \* MERGEFORMAT 

 XE "Test Company Name " \* MERGEFORMAT 

 XE "State " \* MERGEFORMAT 

 XE "Salutation " \* MERGEFORMAT 

 XE "Phone Number " \* MERGEFORMAT 

 XE "PDF file containing Testing Protocol " \* MERGEFORMAT 

 XE "Middle Initial " \* MERGEFORMAT 

 XE "Last Name " \* MERGEFORMAT 

 XE "First Name " \* MERGEFORMAT 

 XE "Fax Number " \* MERGEFORMAT 

 XE "EDR 804 " \* MERGEFORMAT 

 XE "EDR 803 " \* MERGEFORMAT 

 XE "E-mail Address " \* MERGEFORMAT 

 XE "Create/Edit Test Firm " \* MERGEFORMAT 

 XE "City " \* MERGEFORMAT 

 XE "Address Line 2 " \* MERGEFORMAT 

 XE "Address Line 1 " \* MERGEFORMAT Create/Edit Test Firm (EDR 803/804)
The Create/Edit Testing Firm page records information about the firm that will conduct tests at your facility.  If you will have more than one firm conducting tests, you must submit a separate test protocol for each testing firm.

To add or edit a testing firm, follow the instructions for each field, as listed below.  

[image: image77.jpg]Commonvealth of Pennsylvania
ent of Environmental Protection I’
g Bureau of Air Quality

Home ~-> it Test Protacel --> Ect Test Fim

Edit Test Firm

EDR 903 EDR 004

“Send essage View Notes | Ad Note

- View AllMessages

Test Company Name: [Test Firm At
2008-11-27 00:00:000 Test Purpose: Initial Cortification of CEMS <]

 From mTuser POF fe crtainng
| Tesngmeoen . L |[Bowe] eoreosit

To: EXTUSER

et Contact Informat
|205-1127 000000 Sabtation
From: INTUSER. et N
To: EXTUSER
Wil o
his 5 3 ongersubject
Last Name:
Tite: EOPresident
Address Line 01 Horth Second St.

Address Line 2
cy Reading
state: Pennsylvani

p Cote:

A

Phane Humier:

Fax Number:

E-mail Acress:

A Dept. of Enviranmantal Protection DEP Home | CEM Home | Contacts | Help | Logout]

For assistance, please call DEP at (717) 7053768
between the hours of £:00 AM to 430 PM or send an e-mail to
ep-efactshelpdeskteam@state. pa.us.





	Field Label/Link
	Activity

	View Notes
	Clicking the View Notes link opens the View Notes page, which allows you to view all notes associated with this item.

Note:  This link is active only in the online CEMDPS application.  

	Add Note
	Clicking the Add Note link opens the Add Note page, which allows you to enter a note for this item.

Note:  This link is active only in the online CEMDPS application.  

	Test Company Name
	Enter the testing company name.

	Test Purpose


	Use the drop-down list to enter the appropriate one-character code describing the purpose of the test as follows:

· Diagnostic (D)

· Initial Certification (of new or revised CEMS) (I)

· Periodic Self-audit (P)

	PDF file containing Test Protocol


	Click the Browse button to select a file to attach to the test protocol.  The file you choose displays in the text box.  If you previously attached a file, the file name displays as a link.  Click on the file name link to view the previous attachment.

	Salutation
	Enter the preferred correspondence salutation for the test company contact person (for example “Dear Mr. Smith:”).

	First Name
	Enter the first name of the test firm contact person.

	Middle Initial
	Enter the middle initial of the test firm contact person. If the test firm contact person has no middle initial, leave this field blank.

	Last Name
	Enter the last name of the test firm contact person.

	Title
	Enter the title of the test firm contact person.

	Address Line 1
	Enter the first line of the street address of the test company contact person.

	Address Line 2
	Enter the second line of the street address of the test company contact person.

	City
	Enter the city name of the test company contact person.

	State 
	Use the drop-down list to select the state for the test company contact person.

	Zip Code
	Enter the 5-digit zip code of the test company contact person and the 4-digit zip plus 4 code.

	Phone Number
	Enter the phone number for the test company contact person.

	Fax Number
	Enter the fax number for the test company contact person.  If the test company contact person has no fax, leave this field blank.

	E-mail Address
	Enter the e-mail address of the test company contact person.  If the test company contact person has no E-mail address, leave this field blank.


	Button
	Description

	Save
	Clicking Save saves the information and returns you to the Test Protocol page. 

	Cancel
	Clicking Cancel returns you to the Test Protocol page without saving changes.


 XE "Zip Code " \* MERGEFORMAT 

 XE "Title " \* MERGEFORMAT 

 XE "State " \* MERGEFORMAT 

 XE "Salutation " \* MERGEFORMAT 

 XE "Registered Laboratories " \* MERGEFORMAT 

 XE "Phone Number " \* MERGEFORMAT 

 XE "PA Environmental Lab Accreditation Act Registration Number " \* MERGEFORMAT 

 XE "Middle Initial " \* MERGEFORMAT 

 XE "Last Name " \* MERGEFORMAT 

 XE "First Name " \* MERGEFORMAT 

 XE "Fax Number " \* MERGEFORMAT 

 XE "EDR 806 " \* MERGEFORMAT 

 XE "EDR 805 " \* MERGEFORMAT 

 XE "E-mail Address " \* MERGEFORMAT 

 XE "Create/Edit Analytical Laboratory " \* MERGEFORMAT 

 XE "Company Name " \* MERGEFORMAT 

 XE "City " \* MERGEFORMAT 

 XE "Address Line 2 " \* MERGEFORMAT 

 XE "Address Line 1 " \* MERGEFORMAT Create/Edit Analytical Laboratory (EDR 805/806)
The Create/Edit Analytical Laboratory page records information about the analytical laboratories your testing firm uses.  If the firm uses multiple analytical laboratories, you must enter and save information using this page for each laboratory.  If your testing firm is also conducting analysis, you must enter your testing firm as a laboratory in this page.

To add or edit an analytical laboratory, follow the instructions for each field, as listed below.  
[image: image78.jpg]B;mmonwealm‘oﬂunmylvanla
nt of Environmental Protection
Bureau of Air Quality

To: EXTUSER

2008-11-27 00:00:000
From: INTUSER.
To: EXTUSER

i 5 3 longersubject

Home ~-> Eit Test Protacel --> Ect Anaytical Leborstary

Edit Analytical Laboratory

EDR 405 EDR 006

View Notes | Ad Note

Company Name:

P Environmental Leb
Aceredilation Act
Registration Number:

Contact Information
Sebtation:

First Name:
ikl it
Last Nare:
Tt

Adiress Line 1
Adivess Line 2
cty.

State:

Zn Cote:
Phane Nunber.
Fax b

E-mall Actress:

[save]

Registered Lahoratories

P4 Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (717) 7053768
between the hours of £:00 AM to 430 PM or send an e-mail to
ep-efactshelpdeskteam@state. pa.us.





	Field Label/Link
	Activity

	View Notes
	Clicking the View Notes link opens the View Notes page, which allows you to view all notes associated with this item.

Note:  This link is active only in the online CEMDPS application.  

	Add Note
	Clicking the Add Note link opens the Add Note page, which allows you to enter a note for this item.

Note:  This link is active only in the online CEMDPS application.  

	Company Name
	Enter the analytical laboratory company name.

	PA Environmental Lab Accreditation Act Registration Number
	Enter the PA Environmental Laboratory Accreditation Act Registration Number of the analytical laboratory in either ##-### or ##-#### format. 

	Salutation
	Enter the preferred correspondence salutation for the analytical laboratory contact person (for example "Dear Mr. Smith:”).

	First Name
	Enter the first name of the analytical laboratory contact person.

	Middle Initial
	Enter the middle initial of the analytical laboratory contact person. If the analytical laboratory contact person has no middle initial, leave this field blank.

	Last Name
	Enter the last name of the analytical laboratory contact person.

	Title
	Enter the title of the test firm contact person.  If the test firm contact person has no title, leave this field blank.

	Address Line 1
	Enter the first line of the street address of the analytical laboratory contact person. 

	Address Line 2
	Enter the second line of the street address of the analytical laboratory contact person.  If there is no second line of the street address, leave this field blank.

	City 
	Enter the city name of the analytical laboratory contact person.

	State
	Enter the state for the analytical laboratory contact person.

	Zip Code
	Enter the 5-digit zip code of the analytical laboratory contact person.

	Phone Number
	Enter the 10-digit phone number for the analytical laboratory contact person.

	Fax Number
	Enter the 10-digit fax number for the analytical laboratory contact person.  If the analytical laboratory contact person has no fax, leave this field blank.

	E-mail Address
	Enter the e-mail address of the analytical laboratory contact person.  If the analytical laboratory contact person has no e-mail address, leave this field blank.

	Registered Laboratories
	Click this link to view a list of registered environmental laboratories on the DEP web site.


	Button
	Description

	Save
	Clicking Save saves the information and returns you to the Test Protocol page. 

	Cancel
	Clicking Cancel returns you to the Test Protocol page without saving changes.


 XE "Type " \* MERGEFORMAT 

 XE "Test " \* MERGEFORMAT 

 XE "Status " \* MERGEFORMAT 

 XE "Source Combination " \* MERGEFORMAT 

 XE "Emission Result " \* MERGEFORMAT 

 XE "EDR 807 " \* MERGEFORMAT 

 XE "Edit CEMS To Be Tested List " \* MERGEFORMAT 

 XE "CEMSID " \* MERGEFORMAT Edit CEMS to Be Tested List (EDR 807)

The Edit CEMS to Be Tested List page displays the CEMS IDs for the CEMS to be tested as part of a test protocol.  

To add or edit a CEMS to be tested, click to add or remove checkmarks in the Test column.  When finished, click Save at the bottom of the page. Descriptions of the columns in the table on the Edit CEMS to Be Tested List page appear in the table below.

[image: image79.jpg]Commonwealth of Pennsylvania

CEMDPS thwtmm of Environmental Protection P

Bureau of Air Quality

- Creste Synchronizetion Files Edit CEMS to be Tested List
Inbox Test camsp o Souee Emission Result T Status
st s 18210 Kin s, Opacity % PRIMARY Inactive:
(FREH - 0000 I s 18210 Kins. Opacity % PRIMARY Inactive:
o
C] 100 newsoues Onacty % PRMARY  Pendng Phase 2





	Column/Link
	Activity

	View Notes
	Clicking the View Notes link opens the View Notes page, which allows you to view all notes associated with this item.

Note:  This link is active only in the online CEMDPS application.  

	Add Note
	Clicking the Add Note link opens the Add Note page, which allows you to enter a note for this item.

Note:  This link is active only in the online CEMDPS application.  

	Test
	Displays a checkbox for each CEMS, allowing you to click to add or remove CEMSs to be tested as part of a test protocol.

	CEMSID
	Displays the CEMS ID for the CEMSs defined for the source combination and emission result listed.

	Source Combination
	Displays the source combination name.

	Emission Result
	Displays the emission result associated with the source combination listed.

	Type
	Indicates whether the CEMS is the Primary CEMS or a Backup or Standby.

	Status
	Indicates the current status of the CEMS.


	Button
	Description

	Save
	Clicking Save saves the information and returns you to the Test Protocol page. 

	Cancel
	Clicking Cancel returns you to the Test Protocol page without saving changes.


 XE "View Submittal " \* MERGEFORMAT 

 XE "Generate EDR " \* MERGEFORMAT Test Protocol Submittal Page

The Test Protocol Submittal page displays when you click the Validate Submittal button in the Test Protocol page to validate data before submitting your protocol.  Depending on the validity of the data you entered, the Test Protocol Submittal page displays two types of information as follows:

· Successful Validation:  If all test protocol data is entered correctly, the Test Protocol Submittal page displays a confirmation that all information is valid for submission.

· List of Errors:  If there is data that fails to meet formatting or business rules for a test protocol submittal, the Test Protocol Submittal page displays a list of the errors for you to correct before submitting the test protocol.  The submittal page indicates the nature of the error (missing data, invalid value, etc.), the element of the protocol containing the error (Analytical Lab, Test Firm, etc.), and if applicable, the field containing invalid data.

Successful Validation

If all data in your test protocol is entered correctly, the Test Protocol Submittal page displays a confirmation that all information is valid for submission.

[image: image80.jpg]C‘ommnwweanhﬁmm‘ylvlnl-
partment of Environmental Protection P

~ Bureau of Air Quality

Quick Links.

- Send Message
- View AllMessages

| 2006-11-27 om.0m008
| From: mTUSER

To EXTUSER

20061127 0000000

From nTusER

To EXTUSER

his 5 3 ongersubject

Home ~-> Edit Test Protacel ~-> Submit Test Pretocel

Test Protocol Submittal

The Test Protocal has been validated successfuly.

[ submitar | [ swmitts oer ][ Generste EoR

P Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (T17) 7053768
between the hours of £:00 AM to 430 PM or send an e-mailto
ep-efactshelpdeskteam@state.pa.us.





Note:  A confirmation that all data has been validated successfully does not indicate that the test protocol has been submitted to the DEP.  It just confirms that all required data is entered, that the data entered is formatted correctly, and that the data follows appropriate business rules in preparation for submittal.

The View Submittal Button

If your test protocol information is validated, the View Submittal button displays.  Clicking this button allows you to view or save a document in PDF format that contains all test protocol information to be submitted to the DEP.  

Note:  You must have Adobe® Acrobat in order to view the PDF document generated from the View Submittal button.

The Submit to DEP Button

If your test protocol information is validated, the Submit to DEP button displays.  Clicking this button submits your test protocol to the DEP for review. When your test protocol is submitted, the Test Protocol Submittal page displays a message confirming that your protocol was submitted.  The Back to Home Page button returns you to the facility home page.

Note:  The Submit to DEP button displays only for users working in the online CEMDPS.  Users working in the disconnected client application must click Generate EDR to create an EDR text file and upload it from the Facility Home Page in the online CEMDPS application.

The Generate EDR Button

If your test protocol information is validated, the Generate EDR button displays.  Clicking this button allows you to view or save a text file containing all EDR information for the test protocol submittal.

Note:  Users working in the disconnected client application should use the Generate EDR to create an EDR text file, then upload the EDR file into the online CEMDPS from the Facility Home Page in the online application.

List of Errors

If there is data that fails to meet formatting or business rules for a test protocol submittal, the Test Protocol Submittal page displays a list of the errors for you to correct before submitting the protocol.  The submittal page indicates the nature of the error (missing data, invalid value, etc.), the element of the protocol containing the error (Test Firm, Analytical Lab, etc.), and if applicable, the field containing invalid data.

[image: image81.jpg]~ Commonwealth of Pennsylvania
ent of Environmental Protection i
Bureau of Air Quality.

- Send Message
- View AllMessages

inbox
| 2006-11-27 om.0m008
| From: mTUSER
o xTusER
| text
|2008-11-27 0000000
From: NTUSER
To EXTUSER

his 5 3 ongersubject

Home ~-> Edit Test Protacel ~-> Submit Test Pretocel

Test Protocol Submittal

The Test Prtocal has errars
Test Protocal 107 : Prapased Test DateFacitty d is Nul - Ener @ valid value
CEMS to be Tested information is missing for Test Protocolf 107
‘AnelticalLabs Infarmetion s missing far Test Potacel# 107

Test Firm information s missing for Test Protocol# 107

P Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (T17) 7053768
between the hours of £:00 AM to 430 PM or send an e-mailto
ep-efactshelpdeskteam@state.pa.us.





The Edit Test Protocol Button

If the Test Protocol Submittal page lists errors with your protocol data, the Edit Test Protocol button appears at the bottom of the page.  Clicking this button returns you to the Test Protocol page, allowing you to correct the errors and validate the submittal again.

Certification Reports

Certification/Test Report Page

The Certification/Test Report page displays information about certification and test reports at your facility and allows you to add or edit tests. Descriptions of the  page's structure and options appear below. 

[image: image82.jpg]_ Commonwealth of Pennsylvania
ent of Environmental Protection
Bureau of Air Quality

~Send Message.
- View AllVessages

T —

| 2008-11-27 000000
[Fom vrusew
To: EXTUSER

e
| 2008-11-27 000000
From: INTUSER.

To: EXTUSER

| s 3longer subject

Home ~-> Edit Certication/Test Report

Certification/Test Report #271

Expand Al | Collapse All
Basic Information
Prinary Facilty I 510331

Company Name:  CASTLE RUBBERLLC

Facity Name:  CASTLE RUBBER LLCEAST BUTLER BORO
Staus: Revision
SubmitedBY: I KUCHARSKI

Remove Certification Test Report

View al llotes for this Certification Report

Basic Information

Test Date: 03282007

Netfstion Oniy: flo
@ CEMS (3) mm s4a
Clck the E buton to expand

@ Analyzers (3) or sas
Clck the E buton to expans

P4 Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (717) 7053768
between the hours of £:00 AM to 430 PM or send an e-mailto
ep-efactshelpdeskteam@state. pa.us.




Basic Information

This section displays the following information:

	Field Label
	Description

	Primary Facility Id
	Displays the facility ID for which the certification/test report is being submitted.

	Company
	Displays the name of the company associated with the test protocol.

	Facility
	Displays the name of the facility associated with the test protocol.

	Status
	Displays the status of the test protocol as follows:

Status

Description

Initiated

A test protocol is considered Initiated if you have begun entering data for your test protocol but have not yet submitted the information for DEP review.  Only facility users may work with the submittal package while it has this status.

Submitted

A test protocol is considered Submitted if you have submitted your test protocol information for DEP review.  Only DEP reviewers and approvers may work with the submitted data when the test protocol has this status.  You will be able to view the information, but not change it.

Submitted (Partial Submittal)

This status is similar to the Submitted status, but is used to identify a partial submittal.  Partial Submittals normally occur with quarterly reports.  

Review

Once you submit your test protocol, the status changes to Review as DEP reviewers examine your submittal.

Revision

If DEP reviewers find issues with a submittal, they may reject it and request that data be changed or verified by the facility.  In this instance, the test protocol is given the status of Revision, and you may revise the information and resubmit the plan.  Only facility users may work with the test protocol information while it has this status.

Review Complete

After reviewers evaluate and render a decision on the test protocol submission, they move the test protocol into Review Complete status.  At this point, the submission is waiting for a DEP approver to login and verify the reviewer's decision.  No one can change the test protocol submission through the CEMDPS application while it has this status.  Approvers automatically receive an email notification indicating that a reviewed submission is awaiting their approval.

Approved

This is the final status of a submission.  This status indicates that an approver approved the decision made by a reviewer.  When the submission enters Approved status, you, and other defined users at your facility, automatically receive an email notification from the CEMDPS.  No one may change the test protocol data through the CEMDPS once it reaches this status.  Facility users and DEP approvers and reviewers may still view the test protocol information through the PDF file.

Hold

A reviewer or approver may place the test protocol submission in Hold status.  The Hold status remains until the submission is reassigned.



	Submitted By
	Displays the name of the person who submitted the test protocol.


	Button
	Description

	Add
	The Add button displays when no submitter information is specified.  Click Add to enter submitter information for the test protocol.  The Create Submitter Information  page displays.

	Edit
	The Edit button displays when submitter information is already specified. Click Edit to edit submitter information for the test protocol.  The Edit Submitter Information  page displays.


The Remove Certification/Test Report Link

The Remove Certification/Test Report link lets you delete the certification/test report.  Clicking this link opens the Delete <Item> page, which allows you to confirm or cancel the deletion.

The View all Notes for this Certification Report Link

The View all Notes for this Certification Report link opens the View Notes page and allows you to view all notes associated with the components of the certification report.  

Note:  The View all Notes for this Certification Report link is available only in the online CEMDPS application.  

Basic Information (for the certification/test report)

This section displays the following information about the certification/test report:

	Field Label
	Description

	Test Date
	Displays the date of the CEMS test.

	Notification Only
	Indicates whether or not the submittal is only a notification.  If the submittal is simply to notify the DEP of the tests and does not include test results, the value is Yes.  If the submittal includes test results, the value is No.


To enter or edit basic information for a certification/test report, click the Edit button to go to the Set Test Date Page.

CEMS

This area lists tested CEMS and test results.  Each CEMS test displays in a purple heading that indicates the CEMSID, type of test, and the Test ID.

· To add a tested CEMS, click the Add button to go to the Add Tested CEMS (EDR 844) page.

· To edit a tested CEMS, click the Edit button for the appropriate CEMS to go to the Edit Tested CEMS (EDR 844) page.

· To remove a tested CEMS, click the Remove button for the appropriate CEMS.

[image: image83.jpg]B CEMS (3)

EIR 844

[18001 - Annual RelAccuracy Test Audit - Test ID 1[_Edt_|[Remore

iai=ciies Reference Method Value Monitoring System Value c:’;:::m“

1 m i s
2 110 108 Yes
s m 21 o

4 m 110 Yes
s 110 m Yes
s 110 110 Yes
i 110 2 N

i 110 m Yes
s 110 140 N

0 110 m Yes
11 110 110 Yes
12 110 m Yes

[18001 - Data Acquisition System Test [Femo.-

Test Results bR 070
MinuteHour __Period llumber __ Reference System Results ___Monitoring System Resuts
Hour 1 i 17
Hour 2 1 1
Hour 3 m 17
Hour 4 1 1
Hour s m "
Hour 6 m m
Hour 7 1 1
Hour s 1 m
Hour s 1 1





[image: image84.jpg][18210 - Operational Test Period [Femo.

Test Results
Number of cantinuous
hours.

wihout conective
AR

170haus




Test Results

The test results section displays results for the different types of tests performed for a CEMS. The contents of this section varies based on the type of test.

· To add or edit test results, click the Edit button next to the appropriate test results section. Clicking Edit takes you to the page necessary for entering information for that type of test.

Analyzers

This area lists tested analyzers and test results.  Each analyzer test displays in a purple heading that indicates the Analyzer ID, type of test, and the Test ID.

· To add a tested analyzer, click the Add button to go to the Add Tested Analyzer (EDR 848) page.

· To edit a tested analyzer, click the Edit button for the appropriate analyzer to go to the Add Tested Analyzer (EDR 848) page.

· To remove a tested analyzer, click the Remove button for the appropriate analyzer.

[image: image85.jpg] Analyzers (3) EDR 848

[925 - Linearity Testing - Test ID 3 [ €ut ][Remowe

Test Resul
Range __ Reading Number Reference Standard Value Analyzer Reading
Low 1 s a7
Low 2 I 443
Low 3 s 452
it 1 993 998
it 2 993 1005
i 3 %03 1004
Hoh 1 1624 1802
Hon 2 1624 1805
Hon 3 1624 1805





[image: image86.jpg][6925 - 7-day Calibration Error Testing [Femove

Test Resuls| e s6s

ZeroUpscale ___ Period llumber Reference Value ng System Value
Upscale 1 E] 1
Upscale 2 50 2
Upscale 3 50 2
Upscale 4 £l 2
Upscale s £l 1
Upscale 3 £l 1
Upscale 7 £ o
zero 1 o £l
zero 2 o El
zero 3 o )
zero 4 o %
zero s o £l
zero 3 o .
zer0 7 o 50





[image: image87.jpg][6025 - Cycle Time Testing - TestID 2[ €t |[Remore

Test Results| g 072

ZeroUpscale Period llumber Minutes Seconds. Cycle Time

zero 1 Mites 1

Upscale 1 Mines 1





Test Results

The test results section displays results for the different types of tests performed for an analyzer.  The contents of this section varies based on the type of test.

· To add or edit test results, click the Edit button next to the appropriate test results section. Clicking Edit takes you to the page necessary for entering information for that type of test.

The Validate Submittal Button

The DEP requires certification/test report data fields to be submitted in specific formats, which are indicated where applicable in the CEMDPS pages, and to follow business rules outlined in the current Continuous Source Monitoring Manual (CSMM).  At the top of the Certification/Test Report page, click Validate Submittal to have the CEMDPS check the data you entered to ensure it's in the proper format and follows CSMM business rules before you submit the report.  After the validation process, the Certification Report/Test Report Submittal page displays. This page either confirms that all data was validated or lists errors that must be addressed before submitting the report.  Please see Certification Report/Test Report Submittal Page for more information.

 XE "View Submittal " \* MERGEFORMAT 

 XE "Generate EDR " \* MERGEFORMAT Certification Report/Test Results Submittal Page

The Certification Report/Test Results Submittal  page displays when you click the Validate Submittal button in the Certification/Test Report page to validate data before submitting your certification report or test results.  Depending on the validity of the data you entered, the Certification Report/Test Results Submittal page displays two types of information as follows:

· Successful Validation:  If all monitoring plan data is entered correctly, the Certification Report/Test Results Submittal page displays a confirmation that all certification/test report information is valid for submission.

· List of Errors:  If there is data that fails to meet formatting or business rules for a certification/test report submittal, the Certification Report/Test Results Submittal page displays a list of the errors for you to correct before submitting the certification/test report.  The submittal page indicates the nature of the error (missing data, invalid value, etc.), the element of the certification/test report containing the error (CEMS, Analyzer, etc.), and if applicable, the field containing invalid data.

Successful Validation

If all data in your certification/test report is entered correctly, the Certification Report/Test Results Submittal page displays a confirmation that all certification/test report information is valid for submission.

[image: image88.jpg]r}ommnnweann}mmymm-
ent of Environmental Protection P

Bureau of Air Quality

- Send Message
- View AllMessages

| 2006-11-27 om.0m008
 From: NTUSER

To: EXTUSER
2008-11-27 00:00:000

From: INTUSER.

To: EXTUSER

his 5 3 ongersubject

Home ~> it Certication Repart Test Resuts ——> Subit Certfcation ReportTest Resuts

Certification Report/Test Results Submittal

The Cert Report has been validated successfully.

[ submitar | [ swmitts oer ][ Generste EoR

P Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (T17) 7053768
between the hours of £:00 AM to 430 PM or send an e-mailto
ep-efactshelpdeskteam@state.pa.us.





Note:  A confirmation that all data has been validated successfully does not indicate that the certification/test report has been submitted to the DEP.  It just confirms that all required data is entered, that the data entered is formatted correctly, and that the data follows appropriate business rules in preparation for submittal.

The View Submittal Button

If your certification/test report information is validated, the View Submittal button displays.  Clicking this button allows you to view or save a document in PDF format that contains all certification/test report information to be submitted to the DEP.  

Note:  You must have Adobe® Acrobat in order to view the PDF document generated from the View Submittal button.

The Submit To DEP Button

If your certification/test report information is validated, the Submit to DEP button displays.  Clicking this button submits your certification/test report to the DEP for review. When your certification/test report is submitted, the Certification Report/Test Results Submittal page displays a message confirming that your certification/test report was submitted.  The Back to Home Page button returns you to the facility home page.

Note:  The Submit to DEP button displays only for users working in the online CEMDPS.  Users working in the disconnected client application must click Generate EDR to create an EDR text file and upload it from the Facility Home Page in the online CEMDPS application.

The Generate EDR Button

If your certification/test report information is validated, the Generate EDR button displays.  Clicking this button allows you to view or save a text file containing all EDR information for the certification/test report submittal.

Note:  Users working in the disconnected client application should use the Generate EDR to create an EDR text file, then upload the EDR file into the online CEMDPS from the Facility Home Page in the online application.

List of Errors

If there is data that fails to meet formatting or business rules for a certification/test report submittal, the Certification Report/Test Results Submittal page displays a list of the errors for you to correct before submitting the certification/test report.  The submittal page indicates the nature of the error (missing data, invalid value, etc.), the element of the certification/test report containing the error, and if applicable, the field containing invalid data.

[image: image89.jpg]Commonwealth of Pennsylvania
ent of Environmental Protection ¥
Bureau of Air Quality

Home ~> it Certication Repart Test Resuts ——> Subit Certfcation ReportTest Resuts

Certification Report/Test Results Submittal

- Send Message
- View AllMessages

Inbox
| 2006-11-27 om.0m008
| From: mTUSER
To EXTUSER

The Cert Report has errors
Cerifcation ReportiTest Resut 289 : roposed Test Date is Nul - Ener a vald value

127 o
From INTUSER
To: EXTUSER

his 5 3 ongersubject

A Dept. of Enviranmantal Protection DEP Home | CEM Home | Contacts | Help | Logout]

For assistance, please call DEP at (T17) 7053768
between the hours of £:00 AM to 430 PM or send an e-mailto
ep-efactshelpdeskteam@state.pa.us.





The Edit Certification Report Button

If the Certification Report/Test Results Submittal page lists errors with your certification/test report data, the Edit Certification Report button appears at the bottom of the page.  Clicking this button returns you to the Certification/Test Report page, allowing you to correct the errors and validate the submittal again.

 XE "Test Date " \* MERGEFORMAT 

 XE "Set Test Date Page " \* MERGEFORMAT 

 XE "Notification Only " \* MERGEFORMAT Set Test Date Page

The Set Test Date page allows you to indicate the test date for a CEMS and whether the submittal is a notification only or includes test result data.

To set a test date, follow the instructions for each field, as listed below.  

[image: image90.jpg]r}ommnnweann}mmymm-
ent of Environmental Protection P

Bureau of Air Quality

Home ~-» Edit Certifiation/Test Report -~ Set Test Date.

Set Test Date

Correspondence Vi Notes | Ad Note

- Send Message

- View AllVessages Test Date: pazszo0r
Inbox Noifcation Only: [lla =]
2008-11-27 00:00:000 Save Cancel

From: INTUSER
To: EXTUSER

(st be muniddyyyy)

2008-11-27 00:00:000
From: INTUSER.
To: EXTUSER

his 5 3 ongersubject

A Dept. of Enviranmantal Protection DEP Home | CEM Home | Contacts | Help | Logout]
For assistance, please call DEP at (T17) 7053768
between the hours of £:00 AM to 430 PM or send an e-mailto
ep-efactshelpdeskteam@state.pa.us.





	Field Label
	Description

	Test Date
	Enter the test date in mm/dd/yyyy format or click the calendar icon to select a date from a calendar.  (See Date Selection for information on using the calendar to choose a date.) 

	Notification Only
	Use the drop-down list to indicate whether or not the submittal is only a notification.  If the submittal is simply to notify the DEP of the tests and does not include test results, choose Yes.  If the submittal includes test results, choose No.


	Button
	Description

	Save
	Clicking Save saves the information and returns you to the Certification/Test Report page. 

	Cancel
	Clicking Cancel returns you to the Certification/Test Report page without saving changes.


CEMS

 XE "Proposed Testing Date " \* MERGEFORMAT 

 XE "EDR 844 " \* MERGEFORMAT 

 XE "Add Tested CEMS " \* MERGEFORMAT Add Tested CEMS (EDR 844)
The Add Tested CEMS page records CEMS test information. You must report this information for each CEMS test at your facility within 10 days of test completion.  

To add a tested CEMS, follow the instructions for each field, as listed below. 

Note:  When editing a tested CEMS, you may only change the Test ID.  Please see the Edit Tested CEMS (EDR 844) help page for more information.

[image: image91.jpg]Commonwealth of Pennsylvania

CEMDPS . Department of Environmental Protection p

Bureau of Air Quality

Home -~ Ect CerlfcatonfTest Report ~->.Ack Tested CEMS
“Home
Add Tested CEMS
DR 0aa
Correspondence ||
~Send Message
View At Hessaes Select cems ( SOUS  fissongesut  Type staus
From INTUSER [C] te2m0 Kins Opacity % PRMARY  Unceriifiec
20061127 000009 [@] 0 wns Opaciy % PRMARY  Cortodon 72007
B [C] ez iz O oSty BACKUP  Cerlifd on 0512812007
s s 3 onger sujct ] amo w2 . PRMARY  Certifd on 0512812007
[€] e uneiz O oSty PRMARY  Cerlifd on 0211312004
[©] w2 e jre— BhCP Cortiodonc292004
] s wire jre—— PRMARY  Uncered
[C] tm0s  untrz NOX IbsiMBtY BACKIP  Uncertifise
[ e wmre jre— BackP CortiedonOT22007
[ o e jre— PRMARY  Cortedon 722007
] ez ez NOx heBtu BACKP  cartied cn 07152007
o] et re— PRMARY  Cortiedon o707
] ez w2 O oSty BACKUP  Certifd on 0512812007
[E] teom iz e PRMARY  Cerlifd on 0612812007
[F] 1m0 untr2 NOX bsMBty BACKUP  Certfisd on 06/28/2007
[C] 1m0s  untrz NOX IbsiMBtY PRIMARY  Certfie on 087292007
[ e wmie jre— BackP cortiedon O4D1R00T
[E] o jre— PRMARY  Cortodon 0412007
O] toms et Opacty PRMARY  Uncated
] e s Opaciy % BAOP  Uncered
[C] tom  rewsrce ooty PRMARY  Uncered
| Annusl Rel Accuracy Test Audt
i | oataacauston System Test
| Operstiona Test Period
| Relaccuracy Test for ntial Cart. (aniy vaiid for Uncertiied CEMS)
Test, =





	Field Label
	Description

	Select
	Click the radio button to select the CEMS being tested.

	CEMSID
	Displays the CEMS ID for each CEMS associated with a source combination.

	Source Combination
	Displays the source combination names for source combinations defined at your facility.

	Emission Result
	Displays the Emission Result the CEMS is associated with.

	Type
	Indicates whether the CEMS is the Primary CEMS or a Backup or Standby.

	Status
	Indicates the current status of the CEMS.

	Test Type
	Clicking a radio button allows you to indicate the type of test performed.

	Test ID
	Use the drop-down list to select a Test ID from 1 to 9.  Use 1 for the first test series completed on the reported date and increment for subsequent test series completed on the same date.


	Button
	Description

	Save
	Clicking Save saves the information and returns you to the Certification/Test Report page.  An entry for the type of test selected appears under the CEMS heading in the Certification/Test Report page.  Click Edit next to the test to enter test information.  See the CEMS section of the Certification/Test Report page for more details.


 XE "New Test ID " \* MERGEFORMAT 

 XE "EDR 844 " \* MERGEFORMAT 

 XE "Edit Tested CEMS " \* MERGEFORMAT 

 XE "Current Test ID " \* MERGEFORMAT Edit Tested CEMS (EDR 844)

The Edit Tested CEMS page allows you to change the Test ID for a tested CEMS. 

To edit a tested CEMS, follow the instructions for each field, as listed below. When finished, click Save at the bottom of the page.

Note that each “child test record” is a row of data for each test run under a single “Test ID.” 

[image: image92.jpg]c h of
EMDPS B of oyttt Proiacicn m

Bureau of Air Quality

Home --» Edit CertificationfTest Report -~ it Test CEMS.

| Edit Tested CEMS
CEMS 18001 - Annual Rel.Accuracy Test Audit

EDR 044

- Send Message
- View AllMessages

[ e ||| s sk s =
Inbox Curtent Test D: 1

2008-11-27 00:00:000
| NewTesto: [1%]
 From: NTUSER

1o pxtuseR =8

| 20061127 smov0n0
From INTUSER

To: EXTUSER

| s 3 onger subjet

A Dept. of Enviranmantal Protection DEP Home | CEM Home | Contacts | Help | Logout]

For assistance, please call DEP at (T17) 7053768
between the hours of £:00 AM to 430 PM or send an e-mailto
ep-efactshelpdeskteam@state.pa.us.





	Field Label
	Activity

	Current Test ID
	Displays the Test ID currently assigned to the tested CEMS.

	New Test ID
	Use the drop-down list to select a new Test ID from 1 to 9.


	Button
	Description

	Save
	Clicking Save saves the information and returns you to the Certification/Test Report page. 


 XE "Used in Calculation " \* MERGEFORMAT 

 XE "Test Run Within Series " \* MERGEFORMAT 

 XE "Reference Method Value " \* MERGEFORMAT 

 XE "Monitoring System Value " \* MERGEFORMAT 

 XE "EDR 852 " \* MERGEFORMAT Non-Opacity RATA Test Data List (EDR 852)

The Non-Opacity RATA Test Data List page displays test information for each run in a series for a Test ID for a CEMS.  You can also edit, remove, or add test run information from this page.

The table below describes the information displayed in the Non-Opacity RATA Test Data List page and the options available. 

[image: image93.jpg]Commonwealth of Pennsylvania
nt of Environmental Protection
L Bureau of Air Quality

Home ~-> Edt Certification/Test Report ~-> it Non-Opacty RATA Test Data List

Non-Opacity RATA Test Data List

CEMS 18001
M oo |
Correspondonce | TestID 1
s DR 052

| - View Allvessages

‘W D e e R N

From nuseR T T " Ves

et 2 110 117 Yes

[ N " o ves

o Extuser s o 1 ves

| o 1o o Yes
: o 121 "o
s o 1 ves
s o 110 "o
o o 1 ves
o o o ves
12 o 1 ves

P4 Dept. of Environmental Protection DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (717) 7053768
between the hours of £:00 AM to 4:30 PM or send an e-mail to
ep-efactshelpdeskteam@state.pa.us.





	Column
	Description

	Test Run within Series
	Displays the test run within the series as an integer 1 through 15.

	Reference Method Value
	Displays the Reference Method Value in units of the emission standard.

	Monitoring System Value
	Displays the Monitoring System Value in units of the emission standard.

	Used in Calculation
	Indicates whether the run is to be used in calculation of results.


	Button
	Description

	Add
	Click Add to enter a new test run for non-opacity RATA test data. The Set Non-Opacity RATA Test Data page displays.

	Edit
	Click Edit next to the appropriate test run to make changes to that run data.  The Set Non-Opacity RATA Test Data page displays.

	Remove
	Click Remove next to the appropriate test run to remove it from the data list. Clicking this link opens the Delete <Item> page, which allows you to confirm or cancel the deletion.


 XE "Used in Calculation " \* MERGEFORMAT 

 XE "Test Run Within Series " \* MERGEFORMAT 

 XE "Set Non-Opacity RATA Test Data " \* MERGEFORMAT 

 XE "Reference Method Value " \* MERGEFORMAT 

 XE "Monitoring System Value " \* MERGEFORMAT 

 XE "EDR 852 " \* MERGEFORMAT Set Non-Opacity RATA Test Data (EDR 852)
The Set Non-Opacity Relative Accuracy Test Audit Data page records information about non-opacity CEMS relative accuracy test audit runs conducted at your facility.  If you run this type of test, you must enter this information for each test performed.
To add or edit Non-Opacity Relative Accuracy Test Audit Data, follow the instructions for each field, as listed below.  
[image: image94.jpg]Correspondence

- Send Message
- View AllMessages

2008-11-27 00:00:000
From: NTUSER

To: EXTUSER
2008-11-27 00:00:000
From: INTUSER.

To: EXTUSER

his 5 3 ongersubject

Home ~> Edt Certification/Test Report ~> Set Nan-Opachy RATA Test Data

Set Non-Opacity RATA Test Data

DR 052
et v R
Test Run witin
Series:
Reference ethad
Vel il
Monioring System
Vale: i
Usedin Caleutor: [Yes =]
Save Cancel

P Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (717) 7053768
between the hours of £:00 AM to 4:30 PM or send an e-mail to
ep-efactshelpdeskteam@state.pa.us.





	Field Label/Link
	Activity

	View Notes
	Clicking the View Notes link opens the View Notes page, which allows you to view all notes associated with this item.

Note:  This link is active only in the online CEMDPS application.  

	Add Note
	Clicking the Add Note link opens the Add Note page, which allows you to enter a note for this item.

Note:  This link is active only in the online CEMDPS application.  

	Test Run Number Within Series
	Use the drop-down list to enter the Test Run Number Within Series as an integer 1 through 15 in I2 format.

	Reference Method Value
	Enter the Reference Method Value, in units of the emission standard, in F13.3 format.

	Monitoring System Value
	Enter the Monitoring System Value, in units of the emission standard, in F13.3 format. 

	Used in Calculation
	If the run is not to be used in calculation of results, use the drop-down list to enter No.  If the run is to be used in calculation of results, use the drop-down list to enter Yes.


	Button
	Description

	Save
	Clicking Save saves the information and returns you to the Non-Opacity RATA Test Data List page. 


 XE "Test Run Within Series " \* MERGEFORMAT 

 XE "Reference Method Value " \* MERGEFORMAT 

 XE "Monitoring System Value " \* MERGEFORMAT Opacity RATA Test Data List (EDR 856)

The Opacity RATA Test Data List page displays test information for each run in a series for a Test ID for a CEMS.  You can also edit, remove, or add test run information from this page.

The table below describes the information displayed in the Opacity RATA Test Data List page and the options available. 

[image: image95.jpg]‘h:“n':nmwe.un‘oimmymm.
nt of Environmental Protection
; Bureau of Air-Quality

Opacity RATA Test Data List

= CEMS 18208
T
Correspondonce | TestID 1
- Send Message R 856

- View AllMessages

Lo | e e e

2061127 0000 within Series
o s T 3 5 —

o ExTusER [_mi] ]
|

1n
|205-1127 0000000

From mTUsER
To: EXTUSER

| i i 2 onger st

A Dept. of Enviranmantal Protection DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (717) 7053768
between the hours of £:00 AM to 4:30 PM or send an e-mail to
ep-efactshelpdeskteam@state.pa.





	Column
	Description

	Test Run within Series
	Displays the test run within the series as an integer 1 through 9.

	Reference Method Value
	Displays the Reference Method Value in units of the emission standard.

	Monitoring System Value
	Displays the Monitoring System Value in units of the emission standard.


	Button
	Description

	Add
	Click Add to enter a new test run for opacity RATA test data. The Set Opacity RATA Test Data page displays.

	Edit
	Click Edit next to the appropriate test run to make changes to that run data.  The Set Opacity RATA Test Data page displays.

	Remove
	Click Remove next to the appropriate test run to remove it from the data list. Clicking this link opens the Delete <Item> page, which allows you to confirm or cancel the deletion.


 XE "Test Run Within Series " \* MERGEFORMAT 

 XE "Set Opacity RATA Test Data " \* MERGEFORMAT 

 XE "Reference Method Value " \* MERGEFORMAT 

 XE "Monitoring System Value " \* MERGEFORMAT 

 XE "EDR 856 " \* MERGEFORMAT 

 XE "DEP CEMS ID Code " \* MERGEFORMAT 

 XE "Date of Test Completion " \* MERGEFORMAT Set Opacity RATA Test Data (EDR 856)
The Set Opacity RATA Test Data page records information about opacity CEMS relative accuracy test audit runs conducted at your facility.  If you run this type of test, you must enter this information for each test performed.

To add or edit opacity RATA test data, follow the instructions for each field, as listed below.  When finished, click Save at the bottom of the page. 

[image: image96.jpg]Horme -~ Edit CertifcationfTest Report - Set Opacty RATA Test Data

Set Opacity RATA Test Data
DR 056
Correspondence
~Send Message
Test Run witin
- View Al Message Teait |
o Reference ethad

5
2006-11-27 000000 Valie:
| From WTUSER Monioring System [
To: EXTUSER Vi
e Save Cancel

2008-11-27 00:00:000
From: INTUSER.
To: EXTUSER

his 5 3 ongersubject

P Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (717) 7053768
between the hours of £:00 AM to 4:30 PM or send an e-mail to
ep-efactshelpdeskteam@state.pa.us.





	Field Label/Link
	Activity

	View Notes
	Clicking the View Notes link opens the View Notes page, which allows you to view all notes associated with this item.

Note:  This link is active only in the online CEMDPS application. 

	Add Note
	Clicking the Add Note link opens the Add Note page, which allows you to enter a note for this item.

Note:  This link is active only in the online CEMDPS application.  

	Test Run within Series
	Use the drop-down list to enter the Test Run Number Within Series as an integer 1 through 9.

	Reference Method Value
	Enter the Reference Method Value in % opacity in F6.2 format.

	Monitoring System Value
	Enter the Monitoring System Value in % opacity in F6.2 format.


	Button
	Description

	Save
	Clicking Save saves the information and returns you to the Opacity RATA Test Data List page. 


 XE "Reference System Results " \* MERGEFORMAT 

 XE "Period Number " \* MERGEFORMAT 

 XE "Monitoring System Results " \* MERGEFORMAT 

 XE "Minute/Hour " \* MERGEFORMAT 

 XE "EDR 878 " \* MERGEFORMAT DAS Test Data List (EDR 878)

The DAS Test Data List page displays CEMS DAS test runs conducted at your facility.  You can also edit, remove, or add test run information from this page.

The table below describes the information displayed in the DAS Test Data List page and the options available. 

[image: image97.jpg]CEMDPS o s

ommonwealth of Pennsylvania

L Bureau of Air Quality

nt of Environmental Protection

Quick Links.

Home.
Creste Synchronization Fies

Horme ~-» Edit CertifiationfTest Report - Edt DAS Test Data List

DAS Test Data List

CEMS 18001
| comespondence | S
~Send Message
oA Voseqee erio erence System onitor em
bl imrtotionr | _Period Reference Syst WMonitoring Syst:
Inbox Humber Results Results

20061127 0000000 vinute 1 11 7
o e vinute 2 1 1
To EXTUSER
5% vinute 3 I "
|205-1127 0000000 inute 4 1 "7
From: NTUSER hirute 5 I "
o ERIE vinute 3 I 11
s i 3 ongersujet
e 7 I 1

vinute s I 1

vinute 9 I 1

Rid

PA Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (717) 705-3768
between the hours of £:00 AM to 4:30 PM or send an e-mail to

ep-efactshelpdeskteam@state.pa.us.





	Column
	Description

	Minute/Hour
	Indicates whether the data is reported in minutes or hours.

	Period Number
	Indicates the Period Number (test run number) as an integer as follows:

· If data is in hours, displays a value from 1 to 9. 

· If data is in minutes, displays a value from 1 to 60.

	Reference System Results
	Indicates the Reference System Results in units of the emission standard.

	Monitoring System Results
	Indicates the Monitoring System Results in units of the emission standard.


	Button
	Description

	Add
	Click Add to enter a new test run for DAS test data. The Set DAS Test Data page displays.

	Edit
	Click Edit next to the appropriate test run to make changes to that run data.  The Set DAS Test Data page displays.

	Remove
	Click Remove next to the appropriate test run to remove it from the data list. Clicking this link opens the Delete <Item> page, which allows you to confirm or cancel the deletion.


 XE "Set DAS Test Data " \* MERGEFORMAT 

 XE "Reference System Results " \* MERGEFORMAT 

 XE "Period Number " \* MERGEFORMAT 

 XE "Monitoring System Results " \* MERGEFORMAT 

 XE "Minute/Hour Flag " \* MERGEFORMAT 

 XE "EDR 878 " \* MERGEFORMAT Set DAS Test Data (EDR 878)

The Set DAS Test Data page records information about CEMS DAS test runs conducted at your facility.  If you run this type of test, you must enter this information for each test performed.

To add or edit DAS Test Data, follow the instructions for each field, as listed below.  

[image: image98.jpg]EMDPS

Commonwealth of Pennsylvania

nt of Environmental Protection

r'T

Ouick Links.

- Send Message
- View AllMessages

2008-11-27 00:00:000

From: INTUSER.

To: EXTUSER

2008-11-27 00:00:000
From: INTUSER.
To: EXTUSER

i 5 3 longersubject

Bureau of Air Quality

Home - Edit Cerlifcation/Test Report - Set DAS Test Data

Set DAS Test Data

DR 070

View Notes | Ad Note

MinuteiHour Fiag:
Period Number:

Reference System
Resuts:

Wonitoring System
Resuts:

[save]

]
[—

17

P4 Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (717) 705-3768
between the hours of £:00 AM to 430 PM or send an e-mail to
ep-efactshelpdeskteam@state. pa.us.





	Field Label/Link
	Activity

	View Notes
	Clicking the View Notes link opens the View Notes page, which allows you to view all notes associated with this item.

Note:  This link is active only in the online CEMDPS application.  

	Add Note
	Clicking the Add Note link opens the Add Note page, which allows you to enter a note for this item.

Note:  This link is active only in the online CEMDPS application.  

	Minute/Hour Flag
	Use the drop-down list to enter whether the data is reported in minutes or hours.

	Period Number
	Report the Period Number (test run number), as an integer as follows:

· If data is in hours (as entered in the Minute/Hour Flag), enter a value from 1 to 9 in I2 format. 

· If data is in minutes (as entered in the Minute/Hour Flag), enter a value from 1 to 60 in I2 format.

	Reference System Results
	Report the Reference System Results in units of the emission standard in F13.3 format.



	Monitoring System Results
	Report the Monitoring System Results in units of the emission standard in F13.3 format. 


	Button
	Description

	Save
	Clicking Save saves the information and returns you to the DAS Test Data List page. 


 XE "Set Operational Test Period Information " \* MERGEFORMAT 

 XE "Number of Continuous Hours without Corrective Maintenance " \* MERGEFORMAT 

 XE "EDR 876 " \* MERGEFORMAT 

 XE "DEP CEMS ID Code " \* MERGEFORMAT 

 XE "Date of Test Completion " \* MERGEFORMAT Set Operational Test Period Information (EDR 876)

The Set Operational Test Period Information page records information about CEMS operational test period test runs conducted at your facility.  If you run this type of test, you must enter this information for each test performed.

To set Operational Test Period Results, enter the Number of Continuous Hours Without Corrective Maintenance as an integer in I3 format.  When finished, click Save. 

[image: image99.jpg]~ Commonwealth of Pennsylvania
ent of Environmental Protection i
Bureau of Air Quality.

- View AllMessages

| 2006-11-27 om.0m008
 From: NTUSER

To: EXTUSER
2008-11-27 00:00:000

From: INTUSER.

To: EXTUSER

his 5 3 ongersubject

- Send Message

Home ~-> Edit CerticationTest Report ~—> Set Operational Test Perod nformation

Set Operational Test Period Information
DR 076

View Notes | Ad Note

Number of cartinuous

ours
wibaut corectve

maintenance:

[Save]

P Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (T17) 7053768
between the hours of £:00 AM to 430 PM or send an e-mailto
ep-efactshelpdeskteam@state.pa.us.





Analyzers

 XE "UOM " \* MERGEFORMAT 

 XE "Test Type " \* MERGEFORMAT 

 XE "Test ID " \* MERGEFORMAT 

 XE "Status " \* MERGEFORMAT 

 XE "Select " \* MERGEFORMAT 

 XE "Parameter " \* MERGEFORMAT 

 XE "Monitoring Point Code " \* MERGEFORMAT 

 XE "Moisture Basis of Measurement " \* MERGEFORMAT 

 XE "EDR 848 " \* MERGEFORMAT 

 XE "Analyzer ID " \* MERGEFORMAT 

 XE "Add Tested Analyzer " \* MERGEFORMAT Add Tested Analyzer (EDR 848)
The Add Tested Analyzer page records information about the type of analyzer tests you're performing at your facility.  You must report this information for each analyzer tested at your facility within 10 days of test completion.  

To add a tested analyzer, follow the instructions for each field, as listed below.  When finished, click Save at the bottom of the page.  

[image: image100.jpg]Commonwealth of Pennsylvania

nt of Environmental Protection
Bureau of Air Quality

CEMDPS "‘. 5

TRy Home ~-> it Certication/Test Report ~—> Ad Tested Analyzer

~Home
- Create Synchronization Fies

Add Tested Analyzer
R 00
| comespondence |
| -Sendessage
| - View Al essages e e i WMonitoring _ Moisture Basis =
R — Selet AnabzerD  Parameter  UOM  pointcode of Measuroment St
| inbox —
T [F] ezes Opasty % ol s Certted on
| From: INTUSER C] e coz % o et Certiied an
|10 xruser =
] e coz % o ory Centodon
|2008-11-27 0000000 [ coz % oz ory Certied on
(o ausen, ] e co2 % o ory Certed on
To: EXTUSER &l
[ co % o oy Certied on
] ea co2 w o2 ory Certed on
] eas o © o ory Certied on
[F] s co2 % o ory Certfied on
] e o % o ory Certied on
] eae co2 % o oy Certied on
] ezes Opasty % o i Uncertfed
] e Opasty % o e Certed on
] ezes Opasty % o N Certed on
] ez Opasty % o N Uncertfed
[F] sm Opacty % o1 nis, Uncertified
] s co2 % o ory Uncered
] e co % o oy Uncertfed
] ews co2 % o ory B
] eas coz % ol ory Certied on
[F] ss0e co2 % o ory Uncertiied
] 7-dey Calbraton Error Testng
Test Type: | cycte Time Testing
| Lineariy Testing
TestiD

Save





	Field Label
	Activity

	Select
	Click the radio button to select the analyzer being tested.

	Analyzer ID
	Displays Analyzer ID for the facility.  

	Parameter
	Displays the parameter/pollutant for the analyzer.

	UOM
	Displays the units of measurement for the analyzer.

	Monitoring Point Code
	Displays the monitoring point code for the analyzer.

	Moisture Basis of Measurement
	Displays the moisture basis of measurement for the analyzer.

	Status
	Indicates the current status of the analyzer.

	Test Type
	Click the radio button to select the type of test being performed. 

· Linearity testing

· 7-day calibration error testing

· Cycle time testing

	Test ID
	Use the drop-down list to select a Test ID from 1 to 9.  Use 1 for the first test series completed on the reported date and increment for subsequent test series completed on the same date.


	Button
	Description

	Save
	Clicking Save saves the information and returns you to the Certification/Test Report page. An entry for the type of test selected appears under the Analyzers heading in the Certification/Test Report page.  Click Edit next to the test to enter test information.  See the Analyzers section of the Certification/Test Report page for more details.


 XE "New Test ID " \* MERGEFORMAT 

 XE "EDR 848 " \* MERGEFORMAT 

 XE "Edit Tested Analyzer " \* MERGEFORMAT 

 XE "Current Test ID " \* MERGEFORMAT Edit Tested Analyzer (EDR 848)

The Edit Tested Analyzer page allows you to change the Test ID for a tested analyzer. 

To edit a tested analyzer, follow the instructions for each field, as listed below. 

Note that each “child test record” is a row of data for each test run under a single “Test ID.” 

[image: image101.jpg]~ Commonwealth of Pennsylvania "
ent of Environmental Protection

Bureau of Air Quality

- Send Message
- View AllMessages

| 2008-11-27 0000000
| From:

To:

| 20061127 0000000
From

To:

his 5 3 longersubject

Home -~ Edit Certification/Test Report ~->Edt Tested Analyzer

Edit Tested Analyzer
Analyzer 6025 - Cycle Time Testing

EDR 040

Hote: iy the TestID fil can be changed. Changes o s fisd will also he applic o the "ol test records”
Curtent Test D: 1

e |
[save]

P Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (T17) 7053768
between the hours of £:00 AM to 430 PM or send an e-mailto
ep-efactshelpdeskteam@state.pa.





	Field Label
	Activity

	Current Test ID
	Displays the Test ID currently assigned to the tested analyzer.

	New Test ID
	Use the drop-down list to select a new Test ID from 1 to 9.


	Button
	Description

	Save
	Clicking Save saves the information and returns you to the Certification/Test Report page. 


 XE "Zero/Upscale " \* MERGEFORMAT 

 XE "Reference Value " \* MERGEFORMAT 

 XE "Period Number " \* MERGEFORMAT 

 XE "Monitoring System Value " \* MERGEFORMAT 

 XE "EDR 868 " \* MERGEFORMAT 7-Day Calibration Error Data List (EDR 868)

The 7-Day Calibration Error Data List page displays analyzer 7-day calibration error data test runs conducted at your facility.  You can also edit, remove, or add test run information from this page.

The table below describes the information displayed in the 7-Day Calibration Error Data List page and the options available. 

[image: image102.jpg]C f i
CEMDPS cmersof onmetalPestion =
Bureau of Air Quality

Home ~-> it Certification/Test Report ~—> it 7-Day Calibraton Evtor Data List

Edit 7-Day Calibration Error Data List
Analyzer 6025

EDR 068

- Send Message

- View MiMessages || [Zerolpscale Period Humber Reference Value Monitoring System Value
(I [ e = T
s o000
| ot 2 s B
o nsen
e e a1 P 2
= e 2 = 2
s onomo B = ;
o e
e ot 2 s !
st 1 s .

e > . w
e | . B
e B . w
2o ! . .
zero > . P
e | . w0
e > . P





	Column
	Description

	Zero/Upscale
	Indicates whether the test is zero or upscale.

	Period Number
	Displays the period number for the test.

	Reference Value
	Displays the reference value for the test.

	Monitoring System Value
	Displays the monitoring system value for the test.


	Button
	Description

	Add
	Click Add to enter a new test run for 7-day calibration error data. The Edit 7-Day Calibration Error Data page displays.

	Edit
	Click Edit next to the appropriate test run to make changes to that run data.  The Edit 7-Day Calibration Error Data page displays.

	Remove
	Click Remove next to the appropriate test run to remove it from the data list. Clicking this link opens the Delete <Item> page, which allows you to confirm or cancel the deletion.


 XE "Zero/Upscale Flag " \* MERGEFORMAT 

 XE "Reference Value " \* MERGEFORMAT 

 XE "Period Number " \* MERGEFORMAT 

 XE "Monitoring System Value " \* MERGEFORMAT 

 XE "EDR 868 " \* MERGEFORMAT 

 XE "Edit 7-Day Calibration Error Data " \* MERGEFORMAT Edit 7-Day Calibration Error Data (EDR 868)

The Edit 7-Day Calibration Error Data page records information about 7-day calibration error test runs conducted on analyzers at your facility.  If you run this type of test, you must enter this information for each test performed.

To add or edit 7-Day Calibration Error Data, follow the instructions for each field, as listed below.  

[image: image103.jpg]~ Commonwealth of Pennsylvania
ent of Environmental Protection i
Bureau of Air Quality.

To: EXTUSER
|205-1127 000000

From: INTUSER.

To: EXTUSER

his 5 3 ongersubject

- Send Message
- View AllMessages

2008-11-27 00:00:000
 From: NTUSER

Home ~-> Edt Certiication/Test Reprt ~—> Edt 7-Day Calbraton Ertor Data

7-Day Calibration Error Data

EDR 068

View Notes | Ad Note

Zerotpscals Flag:  [Upscale <!

Period Numer:

|
Reterercevake: [T ]
| —

Monitoring System
Value:

[save]

P Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (T17) 7053768
between the hours of £:00 AM to 430 PM or send an e-mailto
ep-efactshelpdeskteam@state.pa.us.





	Field Label/Link
	Activity

	View Notes
	Clicking the View Notes link opens the View Notes page, which allows you to view all notes associated with this item.

Note:  This link is active only in the online CEMDPS application.  

	Add Note
	Clicking the Add Note link opens the Add Note page, which allows you to enter a note for this item.

Note:  This link is active only in the online CEMDPS application.  

	Zero/Upscale Flag
	Use the drop-down list to enter Zero or Upscale.

	Period Number
	Enter the period number (sequential day number) as an integer 1 through 7.

	Reference Value
	Enter the reference value in units of measurement in F13.3 format.

	Monitoring System Value
	Enter the monitoring system value in units of measurement in F13.3 format.


	Button
	Description

	Save
	Clicking Save saves the information and returns you to the 7-Day Calibration Error Data List page. 


 XE "Zero/Upscale " \* MERGEFORMAT 

 XE "Period Number " \* MERGEFORMAT 

 XE "Minutes/Seconds " \* MERGEFORMAT 

 XE "EDR 872 " \* MERGEFORMAT 

 XE "Cycle Time " \* MERGEFORMAT Cycle Time Data List (872)

The Cycle Time Data List page displays cycle time data test runs conducted at your facility.  You can also edit, remove, or add test run information from this page.

The table below describes the information displayed in the Cycle Time Data List page and the options available. 

[image: image104.jpg]Commonwealth of Pennsylvania
nt of Environmental Protection

- Send Message
- View AllMessages

2008-11-27 00:00:000
From: INTUSER
To: EXTUSER

20061127 0000000
From: NTUSER
To: EXTUSER

L, BuruuMAlr;?_l—lM

Home > Edit Certiication/Test Report - Edt Cycle Time Data List

Cycle Time Data List
Analyzer 6025
R 072
Zerolpscale __Period liumber___ Minutes Seconds __Cycle Time
zero 1 irutes 1
Upscale 1 Minutes 1

| s 3longer subject

P Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (717) 7053768
between the hours of £:00 AM to 4:30 PM or send an e-mail to
ep-efactshelpdeskteam@state.pa.us.





	Column
	Description

	Zero/Upscale
	Indicates whether the test is zero or upscale.

	Period Number
	Displays the period number of the test.

	Minutes/Seconds
	Indicates whether the cycle time for the test is in minutes or seconds.

	Cycle Time
	Displays the cycle time for the test.


	Button
	Description

	Add
	Click Add to enter a new test run for cycle time data. The Edit Cycle Time Data page displays.

	Edit
	Click Edit next to the appropriate test run to make changes to that run data.  The Edit Cycle Time Data page displays.

	Remove
	Click Remove next to the appropriate test run to remove it from the data list. Clicking this link opens the Delete <Item> page, which allows you to confirm or cancel the deletion.


 XE "Zero/Upscale " \* MERGEFORMAT 

 XE "Period Number " \* MERGEFORMAT 

 XE "Minutes/Seconds " \* MERGEFORMAT 

 XE "EDR 872 " \* MERGEFORMAT 

 XE "Edit Cycle Time Data " \* MERGEFORMAT 

 XE "Cycle Time " \* MERGEFORMAT Edit Cycle Time Data (EDR 872)

The Edit Cycle Time Data page records information about cycle time test runs conducted on analyzers at your facility.  If you run this type of test, you must enter this information for each test performed.

To add or edit Cycle Time Data, follow the instructions for each field, as listed below.

[image: image105.jpg]Commonwealth of Pennsylvania
ent of Environmental Protection ¥
Bureau of Air Quality

- Send Message

- View AllMessages

FrrETe
| From: INTUSER

o ExtuseR
oz 0mm0
rrom ns

o ExtuseR

his 5 3 ongersubject

Horme ~-» Edit CertificationfTest Report - Edt Cycle Time Data

Edit Cycle e Data

DR 072

View Notes | Ad Note

Zorotpscde:  [zer0 =]
period umber: 1|

Miutes Seconds: [Mimites =]
[ —
=2

P Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (T17) 7053768
between the hours of £:00 AM to 430 PM or send an e-mailto
ep-efactshelpdeskteam@state.pa.us.





	Field Label/Link
	Activity

	View Notes
	Clicking the View Notes link opens the View Notes page, which allows you to view all notes associated with this item.

Note:  This link is active only in the online CEMDPS application.  

	Add Note
	Clicking the Add Note link opens the Add Note page, which allows you to enter a note for this item.

Note:  This link is active only in the online CEMDPS application.  

	Zero/Upscale Flag
	Use the drop-down list to enter Zero or Upscale.

	Period Number
	Enter the Period Number (test run number) as an integer 1 through 3.

	Minutes/Seconds Flag
	Use the drop-down list to enter whether the Cycle Time is determined in Minutes or Seconds.

	Cycle Time
	Enter the Cycle Time for the test run in minutes or seconds (according to the value reported in the Minutes/Seconds Flag) in I2 format. 


	Button
	Description

	Save
	Clicking Save saves the information and returns you to the Cycle Time Data List page. 


 XE "Reference Standard Value " \* MERGEFORMAT 

 XE "Reading Number " \* MERGEFORMAT 

 XE "Range " \* MERGEFORMAT 

 XE "EDR 860 " \* MERGEFORMAT 

 XE "Analyzer Reading " \* MERGEFORMAT Linearity Data List (EDR 860)

The Linearity Data List page displays analyzer linearity data test runs conducted at your facility.  You can also edit, remove, or add test run information from this page.

The table below describes the information displayed in the Linearity Data List page and the options available. 

[image: image106.jpg]Commonwealth of Pennsylvani
nt of Environmental Protection P
Bureau of Air Quality

CEMDPS

Home -~ Edit Certiication/Test Report - Edt Linearty Data List

Linearity Data List
Analyzer 6025

EDR 060

Correspondence |

- Send Message

- View &l Mess Range _Reading llumber__ Reference Standard Value __Analyzer Reading

nbox |l = wr

2008-11-27 00:00:000

Hon 2 1624 1805 it

From wTUSER r |2 L w43
o BXTUSER ow s 152
- DU i | %3 R
20061127 0000000 ey — s
s

[ — o 1 1624 1002 e

Hon 3 1624 1805 Edt move

R





	Column
	Description

	Range
	Displays the range of the analyzer.

	Reading Number
	Displays the reading number within range for the analyzer.

	Reference Standard Value
	Displays the reference standard value for the analyzer.

	Analyzer Reading
	Displays the analyzer reading.


	Button
	Description

	Add
	Click Add to enter a new test run for linearity data. The Edit Linearity Data page displays.

	Edit
	Click Edit next to the appropriate test run to make changes to that run data.  The Edit Linearity Data page displays.

	Remove
	Click Remove next to the appropriate test run to remove it from the data list. Clicking this link opens the Delete <Item> page, which allows you to confirm or cancel the deletion.


 XE "Reference Standard Value " \* MERGEFORMAT 

 XE "Reading Number " \* MERGEFORMAT 

 XE "Range " \* MERGEFORMAT 

 XE "EDR 860 " \* MERGEFORMAT 

 XE "Edit Linearity Data " \* MERGEFORMAT 

 XE "Analyzer Reading " \* MERGEFORMAT Edit Linearity Data (EDR 860)
The Edit Linearity Data page records information about each analyzer linearity test run conducted at your facility.  If you run this type of test, you must enter this information for each test performed.
To add or edit Linearity Data, follow the instructions for each field, as listed below.  When finished, click Save at the bottom of the page.

[image: image107.jpg]Correspondence

- Send Message
- View AllMessages

2008-11-27 00:00:000
From: NTUSER

To: EXTUSER
2008-11-27 00:00:000
From: INTUSER.

To: EXTUSER

his 5 3 ongersubject

Home --» Edit CertifiationfTest Report -~ Edt Linearity Data

earity Data

DR 060

View Notes | Ad Note

Range [ =1

ReadingNumber: 1

Reference Standard

Valie: Ll

Analyzer Reading 7.1

Save Cancel

P Dept. of Environmental Protection

DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (717) 7053768
between the hours of £:00 AM to 4:30 PM or send an e-mail to
ep-efactshelpdeskteam@state.pa.us.





	Field Label/Link
	Activity

	View Notes
	Clicking the View Notes link opens the View Notes page, which allows you to view all notes associated with this item.

Note:  This link is active only in the online CEMDPS application.  

	Add Note
	Clicking the Add Note link opens the Add Note page, which allows you to enter a note for this item.

Note:  This link is active only in the online CEMDPS application.  

	Range
	Use the drop-down list to enter the range. The drop-down list contains the valid values for this field.  If the value you need is not in the drop-down list, please contact the DEP to request that a new value be added.

Examples of acceptable values are:

· Zero

· Low

· Mid

· High

	Reading Number
	Enter the Reading Number within range as an integer 1 through 5.

	Reference Standard Value 
	Enter the Reference Standard Value in units of measurement in F13.3 format. 

	Analyzer Reading
	Enter the Analyzer Reading in units of measurement in F13.3 format.


Correspondence

 XE "Work Item " \* MERGEFORMAT 

 XE "To " \* MERGEFORMAT 

 XE "Subject " \* MERGEFORMAT 

 XE "Send Email " \* MERGEFORMAT 

 XE "From " \* MERGEFORMAT 

 XE "Facility Id " \* MERGEFORMAT 

 XE "CC " \* MERGEFORMAT 

 XE "Attachment " \* MERGEFORMAT CEMDPS Correspondence

The CEMDPS Correspondence page provides the ability to send a message to another CEMDPS user regarding a CEMDPS work item or to view a message from another user.  Information displayed and options available on this page appear in the table below.

Note:  The CEMDPS correspondence system is unavailable in the CEMDPS disconnected client application.

Note:  Options on the CEMDPS Correspondence page vary slightly when sending a message and when viewing a message.  Some options are disabled when viewing a message.  The differences in the page when sending or viewing a message are indicated in the table below.

[image: image108.jpg]C‘ommnwweanhﬁmm‘ylvlnl-
partment of Environmental Protection P
~ Bureau of Air Quality

CEMDPS Correspondence

Fron  [EXTUSERSE

[
- View AllWessages

i :

Correspondence

- Send Message

Send Emal

Send Eml

Facity it [oa ]
2006-11:27 0000000

From: MTUSER suiect | ]
1o UsER p— [ Browse.. |

et
2008-11-27 00:00:000

From: INTUSER.

To: EXTUSER

his 5 3 ongersubject

A Dept. of Enviranmantal Protection DEP Home | CEM Home | Contacts | Help | Logout|
For assistance, please call DEP at (717) 7053768
between the hours of £:00 AM to 430 PM or send an e-mail to
ep-efactshelpdeskteam@state.pas..





	Field Label
	Description

	From
	· When sending a message, automatically displays your user ID.

· When viewing a message, displays the user ID of the person who sent the message.

	Send Email
	This option is enabled only when sending a message.  Click to check the Send Email option next to the To or CC fields if you want a copy of the message sent to the user's email address, as defined in the user's profile in Greenport.  In this case, recipients can view the message via the CEMDPS Correspondence page in the CEMDPS application or as a message in their email application. 

Note:  When you click the Send Email option, all recipients in the To or CC fields will receive the message in their email application.  

	Work Item
	· When sending a message, automatically inserts the work item, if applicable, from the page from which you opted to send a message.

· When viewing a message, displays the work item, if applicable, from which the sender created the message.

	Facility ID
	· When sending a message, automatically inserts your facility ID.

· When viewing a message, displays the sender's facility.

	Subject
	· When sending a message, enter the subject of the message.

· When viewing a message, displays the subject of the message.

	Attachment
	· When sending a message, displays the file selected for attachment to the message.  See the description of the Browse button below for information on choosing a file for attachment.

· When viewing a message, displays the attachment file name as a link.  Clicking the file name link opens the attachment.

	<unlabeled text box>
	· When sending a message, enter your message in the large text box.

· When viewing a message, displays the body of the message.


	Button
	Description

	To
	· When sending a message, click To to use the Find User Pop-Up to select the person(s) to receive the message.  See Find User Pop-Up for more information.

· When viewing a message, displays the user IDs of the users to whom the message was sent.

	CC
	· When sending a message, click CC to use the Find User Pop-Up to select the person(s) to receive a copy of the message.  See Find User Pop-Up for more information.

· When viewing a message, displays the user IDs of the users to whom the message was copied.

	Browse
	This button only appears when sending a message.  Click Browse to navigate to the file you want to attach to the message.  When you select a file, the path and file name display in the Attachment text box.

	Send Message
	This button only appears when sending a message.  Click Send Message to send the message to the recipients.


 XE "Search Type " \* MERGEFORMAT 

 XE "Search Key " \* MERGEFORMAT Find User Pop-Up

The Find User Pop-Up displays when you click To when sending a message in the CEMDPS Correspondence page.  The Find User Pop-Up displays over the message page and lets you search for the user IDs of the intended recipients of the message.

To find a CEMDPS user with the Find User Pop-Up, follow the instructions for each field, as listed below. 

[image: image109.jpg]CEMDPS Correspondence
[ Aaminisrationenu_|

Facity it | ]

Suiect | ]

atachmert | [ Bowse.. |

- Send essage

2008-11-27 00:00:000
From:

To:

2008-11-27 00:00:000
From:

= |

his 5 3 longersubject

A Dept. of Enviranmantsl Protection DEP Home | CEM Home | Contacts | Help | Logout]

o s





	Field Label
	Description

	Search Type
	Enter the search type using the drop-down list.  You may search for users by:

· CEMDPS Facility ID - Search by the ID for the facility generated in the CEMDPS.

· Primary Facility ID -  Search by the main ID for the facility generated by the DEP.

· Regional - Search by DEP region.

· All Internal Users - Search within all internal CEMDPS users.

· All External Users - Search within all external CEMDPS users.

	Search Key
	Depending on the Search Type you selected, enter the search criteria for finding users as follows:

· CEMDPS Facility ID - Enter the ID for the facility generated in the CEMDPS. The search returns a list of all users at the facility.

· Primary Facility ID -  Enter the main ID for the facility generated by the DEP. The search returns a list of all users at the facility.

· Regional - Enter a DEP region name.  The search returns a list of all users in that region.

· All Internal Users - If you selected All Internal Users as the Search Type, the Search Key area is disabled.  The search returns a list of all internal CEMDPS users.

· All External Users - If you selected All External Users as the Search Type, the Search Key area is disabled.  The search returns a list of all external CEMDPS users.




	Button
	Description

	Get Users
	Clicking Get Users displays a list of users matching your criteria in the Select Users Pop-Up. If no users match the search criteria, the message "Cannot find a match for the search criteria" appears in the Select Users Pop-Up. 

	Cancel
	Clicking Cancel closes the Find Users Pop-Up without performing a search.


 XE "User Names " \* MERGEFORMAT 

 XE "To " \* MERGEFORMAT 

 XE "Primary Facility Id " \* MERGEFORMAT 

 XE "CC " \* MERGEFORMAT Select Users Pop-Up

The Select Users Pop-Up displays a list of CEMDPS users who match the criteria entered in the Find User Pop-Up.  From this list, you can select users to receive a message.  The selected users' IDs appear in the To or CC fields in the CEMDPS Correspondence page.

To select users to receive a message, follow the instructions for each field, as listed below. 

[image: image110.jpg]To_ CC_User llames Primary Facility Id.

ZADAKIS
OVAKY
AFOLLETTET

ESTEDSH
ESTEDS45

= =1 131 1] (3] [
£
:
£
g
:

(] ]

[ UnSelectAl | [ insert Selected Contacts |





	Column
	Description

	To
	Click to check users to receive the message.

	CC
	Click to check users to receive a copy of the message.

	User Names
	Displays the users matching the search criteria entered in the Find User Pop-Up.

	Primary Facility Id
	Displays the user's primary facility ID.


	Button
	Description

	All
	Clicking All under the To or CC column checks all users to receive the message or a copy of the message.

	UnSelect All
	Clicking UnSelect All removes all checks from the To and CC columns.

	Insert Selected Contacts
	Clicking Insert Selected Contacts inserts users selected in the To and CC columns into the To and CC fields in the message in the CEMDPS Correspondence page.  The Select Users Pop-Up closes automatically when you insert selected users.


 XE "Work Item " \* MERGEFORMAT 

 XE "To " \* MERGEFORMAT 

 XE "Subject " \* MERGEFORMAT 

 XE "From " \* MERGEFORMAT 

 XE "Facility Name " \* MERGEFORMAT 

 XE "Date " \* MERGEFORMAT Messages Page

The Messages page displays a list of messages sent to you from other users.  The subject of each message is a link, which allows you to view the message.   Information displayed and options available on this page appear in the table below.

Note:  The CEMDPS correspondence system is unavailable in the CEMDPS disconnected client application.

[image: image111.jpg]~ Commonwealth of Pennsylvania
ent of Environmental Protection ¥
Bureau of Air Quality

[pate From To Faciity Name [

- Send essage
- View AllMessages

T — | 007710 st BausER  HsuR!

message for HHs
| 2006-11.27 om.0m008 =

s

T e vy Jorinen Jeomes ez
To B =
tisisabongerswbiect || |a00s-1127 0000000 INTUSER [
‘znnn 127 00:00:00.0 INTUSER
P4 Dept. of Envitonmental Protection DEP Home | CEM Home | Contacts | Help | Logout|

For assistance, please call DEP at (717) 7053763
between the hours of £:00 AM to 430 PM or send an e-mail to
ep-efactshelpdeskteam@state.pa.





	Column
	Description

	Date
	Displays the date and time the message was received.

	Subject
	Displays the message subject as a link below the date.  Clicking on the subject link opens the message.

	From
	Displays the user ID of the person who sent the message.

	To
	Displays the user ID of the person who received the message.

	Facility Name
	Displays the name of the sender's facility.

	Work Item
	Displays the work item to which the message pertains.  The work item appears beneath the facility name.

	[image: image112.jpg]


 (paperclip)
	Indicates that the message includes an attached file(s).


Index



%
% of Equiv. Value
56

% of Refer. Value
56

A
Add
84

Add Source Combination
84

Add Tested Analyzer
175

Add Tested CEMS
159

Added by
73

Address Line 1
137, 140, 142

Address Line 2
137, 140, 142

All 1-hr and 1-min avgs, as applicable?
74

All measurements on at least the minimum cycle time?
74

All monitoring system results for Opacity and Temperature reduced to...?
74

All monitoring system results reduced to 1-hr avgs in terms of...?
74

Analytical Technique
56, 118

Analyzer ID
175

Analyzer Reading
185, 186

Analyzers
61

And/Or Code
128

And/Or Flag (for
44

And/Or Standard
56

And/Or Standard (for or'd Standards)
44, 101, 107, 129

Annual relative accuracy test audit to be conducted on all monitoring...?
78

Assigned Date
23

Assigned To
23

Attachment
189

B
Basis of Measurement
38, 41, 52, 56, 94, 118

C
Cal error checks to be conducted following maintenance?
78

Cal error checks to be conducted prior to maintenance if possible?
78

Calibration Error Limit
56

Calibration Error Limit Config
128

Calibration Error Limit ID Code
129

Calibration Error Limit Value - % of Equiv. Value
129

Calibration Error Limit Value - % of Refer. Value
129

Calibration Error Limit Value - Units of Measurmt
129

Calibration gases for monitors with critical orifices approximate sonic...?
78

Calibration gases prepared per EPA Traceability Protocol?
78

Capacity Information Source
41, 87

Cause and time periods for invalid data?
74

Cause, time periods, and magnitude of emissions which exceed...?
74

CC
189, 193

CEM Manual Revision Number
112

CEMS
61

CEMS Manual Revision #
52

CEMS Type
38, 44

CEMSID
15, 84, 144

Certificate of Conformance with ASTM D6216-03 has been obtained
124

Certification Reports File
30

Certification/Test Reports
15

City
137, 140, 142

Comments
23, 74, 78, 89, 137

Company Name
38, 61, 137, 142

Configuration Filter
38

Copies of Phase I application, Phase II protocol, Phase III report...?
74

Corrected To
38, 41, 94

Cover Letter Statements and Signature File
27, 33

Create/Edit Analytical Laboratory
142

Create/Edit Analyzer
118

Create/Edit Analyzer Opacity and Non-Opacity Specification Information
122

Create/Edit Calibration Error Limit
129

Create/Edit CEMS
112

Create/Edit Data Availability Standard Information
107

Create/Edit Emission Result
94

Create/Edit Emission Result Reason
98

Create/Edit Emission Standard Information
101

Create/Edit Non-Opacity Analyzer Specification Information
126

Create/Edit Non-Opacity CEMS Specification Information
116

Create/Edit Opacity Analyzer Specification Information
124

Create/Edit Opacity CEMS Specification Information
114

Create/Edit Source Combination
87

Create/Edit Submitter Information
137

Create/Edit Test Firm
140

Current Test ID
162, 178

Cycle Time
182, 183

Cycles Per Hour, Measure
124

Cycles Per Hour, Record
124

D
Daily cal check to be conducted at 40%-100% of range...?
78

Daily zero and cal to be conducted on all measurement device ranges?
78

Daily zero check to be conducted at 0%-30% of range...?
78

DAS System Accuracy, 1-Hour Averages
114, 116

DAS System Accuracy, 1-Minute Averages
114

Data and results for all tests, audits, and recalibrations?
74

Data Availability Standard
44

Data Availability Standard Config
105

Data Availability Standard for Or'd Standard
44

Data Availability Standard ID Code
107

Data Availability Standard ID Code for Or'd Standard
107

Data necessary for conversion to units of standard?
74

Data Recorder Resolution in % of Equivalent Reading at Emission Level
124, 126

Data Recorder Resolution in Analyzer's Unit of Measurement
124, 126

Data Recorder Resolution in Seconds
124, 126

Data reduction to comply with QA Section of CEMM?
78

Data Substitution Required
94

Data validation to comply with QA Section of CEMM?
78

Date
73, 194

Date of Test Completion
168, 174

DEP Action Required
15

DEP CEMS ID Code
168, 174

DEP ID
41, 52, 56

Description
56

Distance of emission point of monitoring gases to MSML
89

Distance of flue walls from sample acquisition point
89

Distance of nearest downstream disturbance to MSML
89

Distance of nearest pollution control equipment to MSML
89

Distance of nearest upstream disturbance to MSML
89

Download Facility Configuration Data
15

Due Date
23

E
Edit 7-Day Calibration Error Data
180

Edit CEMS To Be Tested List
144

Edit Cycle Time Data
183

Edit General Monitoring Plan Information
89

Edit Linearity Data
186

Edit Monitoring Plan QA Information
78

Edit Record Keeping Information
74

Edit Tested Analyzer
178

Edit Tested CEMS
162

EDR 801
137

EDR 802
137

EDR 803
139, 140

EDR 804
140

EDR 805
142

EDR 806
142

EDR 807
144

EDR 812
84, 87

EDR 820
94

EDR 821
97, 98

EDR 822
100, 101

EDR 823
105, 107

EDR 824
112

EDR 828
118

EDR 829
118

EDR 830
128, 129

EDR 834
114

EDR 835
116

EDR 836
126

EDR 837
124

EDR 840
122

EDR 841
74

EDR 842
78

EDR 843
89

EDR 844
159, 162

EDR 848
175, 178

EDR 852
163, 165

EDR 856
168

EDR 860
185, 186

EDR 868
179, 180

EDR 872
182, 183

EDR 876
174

EDR 878
170, 172

Effective Date
74, 78, 87, 89, 94, 98, 112, 114, 116, 118, 122, 124, 126, 129

E-mail Address
137, 140, 142

Emission Outlet Pathlength
124

Emission Reports
15

Emission Result
15, 52, 61, 84, 144

Emission Standard
44

Emission Standard Config
100

Emission Standard Direction
44, 101

Emission Standard for Or'd Standard
44

Emission Standard ID Code
101, 107

Emission Standard ID Code for or'd Standard
107

Emission Standard Value
44, 101

End Date
44, 100, 101, 105, 107

Equipment Names Attachment
89

Equipment Params Attachment
89

Equivalent diameter of the flue at the monitoring system measurement location (MSML)
89

Equivalent Reading at Emission Standard Level
56, 118

Expected Maximum Reading
124, 126

Expected Normal Reading
124, 126

F
Facility Action Required
15

Facility Configuration
38

Facility Id
189

Facility Name
38, 61, 194

Fax Number
137, 140, 142

F-factors for non-uniform fuels determined per QA Section of CEMM?
78

First Name
137, 140, 142

Flow Diagram Attachment
89

From
189, 194

Fuel Sampling/analysis to determine F-factors?
78

Full Scale Value
56, 118

G
Generate EDR
69, 146, 155

I
ID
38, 41, 44, 52

Is this a Sample Report?
33

L
Last Name
137, 140, 142

Last Update
23

Linearity Limit as % of Reference Value
56, 118

Linearity Limit in Analyzer's Unit of Measurement
56, 118

Linearity test to be conducted if post-maintenance checks...?
78

Location of pollution control equipment relative to MSML
89

M
Manufacturer
56, 118

Manufacturer's claimed 7-day calibration error as % of equivalent ...
122

Manufacturer's claimed 7-day calibration error as % of reference value
122

Manufacturer's claimed 7-day calibration error as unit of measurement
122

Manufacturer's claimed cycle time in seconds
122

Manufacturer's claimed linearity as % of reference value
122

Manufacturer's claimed linearity as unit of measurement
122

Measurement devices to be adjusted if cal error performance...?
78

Middle Initial
137, 140, 142

Minute/Hour
170

Minute/Hour Flag
172

Minutes/Seconds
182, 183

Model Number
118

Moisture Basis of Measurement
175

Monitor Pathlength
124

Monitoring data available via telemetry in accordance with...?
74

Monitoring Plan EDR File
24

Monitoring Plans
15

Monitoring Point Code
38, 52, 56, 118, 175

Monitoring System Results
170, 172

Monitoring System Value
163, 165, 167, 168, 179, 180

Multicomponent gases free from interferents and non-reactive?
78

N
Name
87

New Test ID
162, 178

Note
73

Note Text
72

Notification Only
158

Number of Continuous Hours without Corrective Maintenance
174

Number of Cycles Per Hour, Measure and Record
126

Number of Zero and Calibration Checks per Week
124, 126

O
Offline Client Application
15

Online Facility
15

Opacity Relative Accuracy, 1-Minute Averages
114

Opacity Relative Accuracy, Average of 15 1-Minute Averages
114

Opacity/Non-Opacity
52, 56, 112, 118

Or'd Emission Result ID Code
44, 101

Or'd Emission Standard ID Code
44, 101

P
PA Environmental Lab Accreditation Act Registration Number
142

Parameter
38, 41, 52, 175

Parameter/Pollutant
94, 118

PDF file containing QA Plan
78

PDF file containing Testing Protocol
140

Penalty Factor
52

Penalty Parameter
44, 101

Period Number
170, 172, 179, 180, 182, 183

Phase 1 Submitted
38, 44, 52

Phase 3 Approved
38, 44, 52

Phone Number
137, 140, 142

Plan Approval Number
41, 87

Primary Facility Id
38, 61, 193

Process and control equipment data that affect emissions?
74

Proposed Testing Date
139, 159

Published F-factors used?
78

Q
QA per 40 CFR 75, Appendix D, 2.1.6, & all subparagraphs...?
78

Quarterly high check to be conducted at 80%-100% of range, or higher...?
78

Quarterly linearity to be conducted on all measurement device ranges?
78

Quarterly low check to be conducted at 0%-30% of range or lower...?
78

Quarterly mid check to be conducted at 40%-60% of range near...?
78

Quarterly Reports File
33

R
Range
185, 186

Rated Capacity
41, 87

Reading Number
185, 186

Reason for Information Change
74, 78, 87, 89, 94, 98, 101, 107, 112, 114, 116, 118, 122, 124, 126, 129

Reason for Installation
44, 97, 98

Record of changes to
78

Record of corrective actions in response to exceedances or invalid data?
74

Record of repairs, adjustments, or maintenance?
74

Records of manual adjustments maintained?
78

Reference material/signal to be applied as close to sample acquisition...?
78

Reference Method Value
163, 165, 167, 168

Reference Standard Value
185, 186

Reference System Results
170, 172

Reference Value
179, 180

Registered Laboratories
142

Regulatory Citation
44, 97, 98

Relative Accuracy in Units of Measurement
116

Relative Accuracy vs. emission standard
116

Relative Accuracy vs. reference method
116

Remove <Item>
15

Replace with EDR Upload
15

Report to be submitted by 30th day after quarter close?
74

Reports specified in CEM Manual to be reported on calendar quarter basis?
74

Reports to be submitted in format specified in CEM Manual and signed...?
74

Results from tests, audits, and recalibrations reported on calendar...?
74

Revision #
38, 44, 52, 56

S
Salutation
137, 140, 142

Sample Interface Technique
56, 118

Search Key
191

Search Type
191

Select
175

Send Email
189

Serial Number
56, 118

Set DAS Test Data
172

Set Non-Opacity RATA Test Data
165

Set Opacity RATA Test Data
168

Set Operational Test Period Information
174

Set Proposed Testing Date
139

Set Test Date Page
158

Source Combination
61, 84, 144

Start Date
44, 100, 101, 105, 107

State
137, 140, 142

Status
15, 23, 38, 41, 44, 52, 61, 84, 144, 175

Status Date
23

Subject
189, 194

Submitted By
61

T
Test
144

Test Company Name
140

Test Date
158

Test ID
175

Test Protocol File
27

Test Protocols
15

Test Purpose
140

Test Run Within Series
163, 165, 167, 168

Test Type
175

Thermocouples calibrated using NIST/ASTM procedures...?
78

Time Without Corrective Maintenance
114, 116

Title
137, 140, 142

To
189, 193, 194

Truncation Level
44, 101

Type
15, 38, 52, 84, 112, 144

Type of nearest downstream disturbance
89

Type of nearest pollution control equipment
89

Type of nearest upstream disturbance
89

U
Units
38, 41, 52

Units of Measurement
56, 94, 118

UOM
175

Updated By
23

Upload Client Application Submittal Packet
15

Upload EDR Submittal Packet
15

Used in Calculation
163, 165

User Names
193

V
Validate Submittal
61, 131

Variable Emission Result ID Code
44, 101

View Analyzer
56

View CEMS
52

View Emission Result
44

View History
15

View Source Combination
41

View Submittal
69, 146, 155

View/Edit Details
15

View/Send Correspondence
15

W
Work Item
189, 194

Work Item Assignment Report
23

Work Item ID
23

Work Item Type
23

Z
Zero gases in accordance with QA Section of CEMM?
78

Zero/Upscale
179, 182, 183

Zero/Upscale Flag
180

Zip Code
137, 140, 142



